## RDM Org
ROOM DATA MATRIX | [5 empty] | INTERIOR CONSTRUCTION | [8 empty] | DOORS AND HARDWARE | [6 empty] | MECHANICAL | [9 empty] | ELECTRICAL | [6 empty] | IT
ROOM IDENTIFICATION | [5 empty] | FLOOR |  | WALLS |  |  |  | CEILING |  | NOTES | [7 empty] | Note: Use parameters within FGI Guidelines for the noted FGI Equivalent category, unless noted otherwise. | [9 empty] | POWER |  |  | LIGHTING
Functional Area | DEPARTMENT | ROOM NAME | ROOM NAMES (VA) | FGI EQUIVALENT FOR ASHRAE 170 | FGI EQUIVALENT FOR TABLE 1.2-5 Minimum Sound Isolation | Floor Finish | Base | Wall Finish | Wainscot Material | Wainscot Height | STC | Ceiling Finish | Height | Notes | Size (Width) | Type | Material | Glazing | Rating | Hardware Group | Hardware Notes | Indoor Temperature Cooling F | Indoor Temperature Heating F | Indoor Relative Humidity % RH Max | Indoor Relative Humidity % RH Min | Minimum Total ACH | Minimum OA ACH | Room Air Return Gen. Exh G Spec Exh S | Maximum Noise Level NC | Room Air Balance | HVAC Notes | # Duplex Receptacles | # Quad Receptacles | Power - Notes | Fixture Type | Controls | Lighting - Special Requirements | Lighting - Notes | # Data Outlets (standard density WAO) | IT - Special Requirements
0 | General Rooms/Spaces | Exam Room | PACT Exam | EXAM | EXAMINATION | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | 10 | 3'-0" --------------- 3'-6" | Flush | Wood | _ | _ | 12 SE | 3 | [10 empty] | 8 | 1 |  |  | Multilevel Switching, Dimming & Occupancy | Multi-level switching or manual dimming | N/A | 3
0 | General Rooms/Spaces | Exam Room | Exam Room - Multi-Specialty, Exam / Treatment, Exam - Consult, Consult Room - PACT, Exam/Consult Room (Mental Health/Social Work), Exam Room EMG/EEG, Exam Room-Cardiology, Exam/Consult, Nurse Practitioner, Women's Health Exam, Tele-Health Exam, Optometry Exam Treatment Room, Eye Lane, Tele-Retinal, TECHS, Applicance Fitting Room, Fitting Room, Physical Therapy Room, Occupational Treatment Room | EXAM | EXAMINATION | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | 10 | 3'-6" | Flush | Wood | _ | _ | 12 S | [11 empty] | 8 | 1 |  |  | Multilevel Switching, Dimming & Occupancy | Multi-level switching or manual dimming | N/A | 3
0 | General Rooms/Spaces | Consult Room | Consult Room, Audiology Rehabilitation Counceling Room, Dental Consult Room |  | CONSULTATION | CPT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | -- | 3'-6" | Flush | Wood | _ | _ | 12 S | _ | 75 | 70 | 60 | - | 4 | 2 | Return | 40 | NR |  | 6 |  |  |  | Multilevel Switching, Dimming & Occupancy | Multi-level switching or manual dimming | N/A | 1
0 | General Rooms/Spaces | Procedure Room | Procedure Room, General, Urology, Gynecology, Specialty Care, Multi-Specialty Care, Cast Room | PROCEDURE | TREATMENT | WSF | WSF | EP | RWC | 4'-0" | SEE FGI | AT | 9'-0" | 3 | 3'-0" --------------- 3'-6" | Flush | Wood | -- | -- | 12 SE | 3 | [10 empty] | 7 |  | P13 |  | Multilevel Switching, Dimming & Occupancy | Wall mounted exam light | N/A | 2
0 | General Rooms/Spaces | Laboratory | Laboratory (Typical) | LABORATORY WORKROOM | __ | WSF | WSF | EP | -- | -- | 40 | AT-SP | 9'-0" | 3 | 3'-0" | Flush | Wood | _ | _ | 15 AG | 4 | [10 empty] | 6 |  | P3, P4 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 5
0 | General Rooms/Spaces | Conference Room | Conference Room, Multi-Purpose Room, Group Room, Shared Medical Appointment Room, Education Room, Staff Training Room, Classroom |  | __ | CPT | RB | P | RWC | 4'-0" | 40 | AT | 9'-0" | 17 | 3'-6" | Flush | Wood | _ | _ | 15 S | _ | [9 empty] | M2 | 8 |  | P14 |  | Multilevel Switching, Dimming & Occupancy | Provide 4 scene preset dimmable lighting for a variety of tasks. Consider placement and optics to mitigate glare and ceiling reflections. | N/A | 4 | Floor data for table
0 | General Rooms/Spaces | TOILET | General Toilet, Patient - Toilet, Toilet - Police, Toilet - Family, Toilet - Female Staff, Toilet - Male Staff, Toilet - Procedure Room, Toilet - Public, Toilet - RF Patient, Toilet - Women's Health, Toilet - Female, Toilet - Family Assist, Specimen Collection Toilet | TOILET ROOM | TOILET ROOM | PT | PT | P | CT | 7'-0" | SEE FGI | AT | 9'-0" | 1,2 | 3'-6" | Flush | Wood | _ | _ | 11 | _ | [10 empty] | 1 |  |  | Downlights/Mirror or vanity | Occupancy Sensor | N/A | N/A
0 | General Rooms/Spaces | OFFICE | Any Office | -- | CONSULTATION | CPT | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 12 CS | [11 empty] | 4 | 1 |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
0 | General Rooms/Spaces | WAITING | Waiting - Family - PACT, Waiting - PACT 3, Waiting - General - 20 People, Waiting - General - 10 People, Waiting - General - 6 People, Waiting-General |  | EXAM - PUBLIC SPACE | CPT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | 10, 17 | [16 empty] | M4 | -- | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
0 | General Rooms/Spaces | RECEPTION | Reception, Information Desk, Travel Window, Reception - Accessible | -- | -- | RFT | RB | P | -- | -- | -- | AT | 9'-0" | -- | 3'-0" | Flush w/ narrow vision | Wood | _ | _ | 12 CG | 3 | [9 empty] | M4 | 1 | 1 |  | Downlights, pendants, decorative, and accent | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 10 | Data/phone feeds to systems furniture
0 | General Rooms/Spaces | COPY ALCOVE | Copy Alcove, Copier - Workroom, Copy / Office Supply Room, Copy Room | -- | -- | RFT | RB | P | -- | -- | -- | AT | 9'-0" | 6 | _ | _ | _ | _ | _ | _ | 6 | [10 empty] | 3 |  |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 3
0 | General Rooms/Spaces | CLEAN UTILITY | Clean Utility, Clean Supply, Clean Workroom, Clean Linen, Sterile Storage, CBOC Steril Supply Storage Room, Clean Scope, Dental Clean Cart, Central Sterile | -- | -- | RFT | RB | P | RWC | 4'-0" | -- | AT | 9'-0" | -- | 3'-0" | Flush | Wood | -- | 45 MIN | 121 AG | _ | 66 | 75 | 55 | 30 | 4 |  |  |  | (+) |  | 1 |  |  |  | Occupancy Sensor | N/A | N/A
0 | General Rooms/Spaces | SOILED UTILITY | Soiled Utility Room, Recycled Material, Soiled Holding, Soiled Linen, Soiled Workroom, Soiled Supply, Soiled Cart | SOILED HOLDING / SOILED WORK ROOM | -- | WSF | WSF | P | RWC | 4'-0" | -- | AT | 9'-0" | 3 | 3'-0" | Flush | Wood | -- | 45 MIN | 121 AG | _ | [10 empty] | 2 | -- |  |  | Occupancy Sensor | N/A | N/A | --
0 | General Rooms/Spaces | STORAGE | Storage - Medical Equipment, Storage - Shared Medical Appointments, DME - Prosthetics Storage, Storage - Homeless, EMS Storage, Storage - Bistro/Coffee Bar, Storage - Patient Clothing and Luggage, Laundry / Storage, Tray Cart Storage Area, Buld Storage, General Storage, Secure Storage, | CLEAN WORKROOM/CLEAN SUPPLY |  | RFT | RB | P | -- | -- | -- | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | 35 AG | [11 empty] | 1 per wall, not to exceed 12' spacing | -- |  | Surface or chain mounted 1' x 4' | Occupancy Sensor | N/A | N/A
0 | General Rooms/Spaces | JANITOR'S CLOSET | Housekeeping Aides Closet (HAC) | ENVIRONMENTAL SERVICES ROOM | -- | CS | RB | P | FRP | 4'-0" | -- | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | 34 A | _ | [10 empty] | 1 | -- |  |  | Occupancy Sensor | N/A | N/A | --
0 | General Rooms/Spaces | KITCHENETTE | Social Activities Space/ Kitchen | -- | -- | RFT | RB | P | -- | -- | -- | AT | 9'-0" | 17 | 3'-0" | Flush | Wood | -- | -- | 15 A | _ | [10 empty] | 4 | -- |  |  | Multilevel switching/dimming/occupancy | N/A | N/A | --
0 | General Rooms/Spaces | EQUIPMENT ALCOVE | AED Alcove, Height and Weight Alcove, Scale Alcove, Stretcher Alcove, Med Alcove, Portable Patient Lift Alcove, Wheelchair Alcove, My Health eVet, Kiosk, | -- | -- | Match Adjacent | Match Adjacent | Match Adjacent | RWC | 4'-0" | -- | AT | Match Adjacent | 3 | -- | -- | -- | -- | -- |  | 6 | [10 empty] | 1 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | --
0 | General Rooms/Spaces | STAFF LOUNGE | Staff Lounge | -- | -- | RSF | RB | P | -- | -- | 40 | AT | 9'-0" | 4 | 3'-0" | Flush w/ narrow vision | Wood | -- | -- | 13 | _ | [6 empty] | Exh. (G) |  | (-) |  | 8 | -- | P7 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
0 | General Rooms/Spaces | MEDICATION ROOM | Medication Room | MEDICATION ROOM | -- | RFT | RB | P | -- | -- | -- | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | 34 | [11 empty] | 5 | 1 |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
0 | General Rooms/Spaces | LACTATION ROOM | Employee Wellness, Lactation Room, Quiet Room | -- | -- | RFT | RB | P | -- | -- | 50 | AT | 9'-0" | 10 | 3'-0" | Flush | Wood | -- | -- | 12 CS | [11 empty] | 4 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
0 | General Rooms/Spaces | LOCKER ROOM | Locker Room, Locker Room (Male/ Female) Locker - Staff Personal Property, Locker Room - Staff | -- | -- | RFT | RB | P | -- | -- | 40 | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | Push/Pull | [7 empty] | Exh. (G) |  | (-) |  | 4 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | --
0 | General Rooms/Spaces | OFFICE, CUBICLE, Open Office | Cubicle - Administrative, Data Processing, Workstation - Extended Team, Homeless, Workstation - MICHM, Workstation - Suicide Prevention, Workstation - VOC Rehab, Workstation - Rad Tech, Workstation - Shipping / Receiving, Workstation, Administration (MSA MH; Rad, LPN), Workstation-Sleep Tech, Work Station, Call Center (MSA), Workstation-Cart Case Dispatch, Workstation-Clerical, | -- | -- | CPT | RB | P | -- | -- | -- | AT | 9'-0" | [18 empty] | 2 per workstation | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
0 | General Rooms/Spaces | SUB-WAITING | Sub-Waiting, MRI Sub-Waiting, CT Sub-Waiting, Mammo Sub-Waiting, Sub-Waiting - Diagnostic Patient, Sub-Waiting - Dilation Patient, CT Vestibule, Waiting, Waiting-Zone 1, Sub-Waiting-Zone 2 | -- | -- | CPT | RB | P | -- | -- | -- | AT | 9'-0" | 2019-10-17 | -- | -- | -- | -- | -- | - | 6 | [9 empty] | M4 | 4 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | --
0 | General Rooms/Spaces | VENDING | Vending Machine Area |  |  | RFT | RB | P | -- | -- | -- | AT | 9'-0" |  | -- | -- | -- | -- | -- | -- | 6 | [9 empty] | M4 | 8 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 4
0 | General Rooms/Spaces | TOILET/SHOWER ROOM | Toilet/Shower-Staff, Toilet/Shower-Patient, Toilet/Shower-Female Staff, Toilet/Shower-Male Staff | TOILET ROOM | TOILET ROOM | PT | PT | CT | -- | -- | SEE FGI | GWB/P | 9'-0" | 2, 19 | 3'-6" | Flush | Wood | -- | -- | 11 G | [11 empty] | 2 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A
0 | General Rooms/Spaces | CHANGING ROOM | Dressing room |  |  | RFT | RB | P | -- | -- | 40 | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 11 K |  | 75 | 70 | 60 | - | 4 | 2 | Return | NR | NR |  | 1 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A
2 | Primary Care, Specialty Care, PACT | PACT TEAM WORK SPACE | PACT Team Work Space, Team Work Area- Home Based Primary Care |  | -- | CPT | RB | P |  |  | -- | AT | 9'-0" | -- | _ | _ | _ | _ | _ | 14 MP | 6 | [9 empty] | M3 | 2 per workstation | -- |  |  | Multilevel Switching, Dimming & Occupancy | Provide dimming and switching to provide various light levels. Provide switching in refraction desk to control overhead lighting. | N/A | 1 per workstation
2 | Primary Care, Specialty Care, PACT | EXAM ROOM, AIRBORNE INFECTION ISOLATION | Exam, Isolation, Negative Pressure | AII Room | EXAMINATION | WSF | WSF | P | -- | -- | SEE FGI | GWB:P | 9'-0" | 3,7 | 3'-6" | Flush | Wood | -- | -- | 12 S | [11 empty] | 6 | -- |  |  | Multilevel Switching, Dimming & Occupancy | Sealed fixture, flat lens surface on exterior | N/A | 1
5 | Audiology and SLP | AUDIOLOGY HEARING AID TESTING | Hearing Aid Lab, Hearing Aid Processing, Hearing Aid Repair |  | -- | RFT | RB | P | -- | -- | 40 | AT | 9'-0" | -- | 3'-0" | Flush | Wood | _ | _ | 15 S | _ | 75 | 70 | 60 | - |  |  | Exh. (G) |  | (-) |  | 7 | 0 | P4 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
5 | Audiology and SLP | AUDIOLOGY HEARING AID FITTING | Audiology Programming / Fitting, Hearing Aid Fitting Room, Cerumen Management Room, Speech Language Pathology Assistive Technology Romm, Speech Language Pathology Voice Treatment Room | EXAM | -- | CPT | RB | P | -- | -- | 60 | AT | 9'-0" | -- | 3'-6" | Flush | Wood | _ | _ | 12 S | _ | [10 empty] | 6 |  |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
5 | Audiology and SLP | AUDIOMETRIC EXAM BOOTH | Audiometric Exam Suite, Exam - Audiometric Booth, Aud: Suite - Audiometric Exam, Hearing/Diagnostics, Booth, 1-Person | EXAM | -- | Pre-Fab | Pre-Fab | Pre-Fab | -- | -- | SEE EQUIP LIST | Pre-Fab | 8'-0" | -- | 3'-0" --------------- 3'-6" | Pre-Fab | Pre-Fab | _ | _ | 1 | 2,4 | [10 empty] | 9 |  | P1 |  | Typically pre-packaged unit including lighting and switching | N/A | L1 | 5
5 | Audiology and SLP | ELECTROPHYSIOLOGY | Electrophysiology, Posturography, Vestibulography | EXAM | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | -- | 3'-6" | Flush | Wood | _ | _ | 12 S | _ | [10 empty] | 6 |  | P2, P3, P14 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 3
6 | Dental Service | SPECIALTY EQUIPMENT MECHANICAL ROOM | Dental Equipment Mech. Room, Mechanical Rooms - Electrical | -- | -- | CS | -- | P | -- | -- | 60 | EXP | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 14 S | [7 empty] | Exh. (G) |  | (-) |  | 2 | -- | P3 | Surface or chain mounted 1' x 4' | Occupancy/vacancy | N/A | N/A | 1
6 | Dental Service | DENTAL PROSTHETICS LABORATORY | Laboratory, Dental Prosthetics |  | -- | WSF | WSF | P | -- | -- | -- | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | 15 AG |  | 75 | 70 | 60 | 20 | 6 | 2 | Return Exh. (G) | 45 | (-) | M13 | 7 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 5
6 | Dental Service | DENTAL TREATMENT ROOM | Dental Treatment Room (DTR), Multi-Functional (4/Hygiene), Special Needs Patient, Bariatric | EXAM | TREATMENT | WSF | WSF | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 12 CS | [9 empty] | (+) |  | 7 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
6 | Dental Service | DENTAL X-RAY ROOM | X-Ray Room, Panoramic / Cephalometric (Cone Beam) | CLASS 1 IMAGING ROOM | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | 5 | 3'-6" | Flush | Wood | -- | LEAD LINED | 17 AGL | 8 | [10 empty] | 7 | -- | P3 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
7 | Optometry | FITTING & DISPENSING, EYEGLASSES | Fitting & Dispensing, Eyeglasses |  | -- | RFT | RB | P | -- | -- | -- | AT | 9'-0" | -- | 3'-6" | Flush | Wood | _ | _ | 12 S | 6 | 75 | 70 | 60 | - | 4 | 2 | Return | 40 | NR |  | 2 |  |  | Downlights and accent/display | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
7 | Optometry | LOW VISION EXAM/ THERAPY/ TRAINING | Low Vision Exam/ Therapy/ Training | EXAM | EXAMINATION | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | -- | 3'-6" | Flush | Wood | _ | _ | 12 S | _ | [10 empty] | 6 |  |  |  | Multilevel Switching, Dimming & Occupancy | Provide dimming and switching to provide various light levels. Provide switching in refraction desk to control overhead lighting. | N/A | 3
7 | Optometry | PRE-TESTING/ INTAKE | Pre-Testing/ Intake | EXAM | EXAMINATION | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | -- | 3'-6" | Flush | Wood | _ | _ | 12 S | _ | [10 empty] | 6 | 1 |  |  | Multilevel Switching, Dimming & Occupancy | Provide dimming and switching to provide various light levels. Provide switching in refraction desk to control overhead lighting. | N/A | 2
7 | Optometry | VISUAL FIELDS ROOM | Visual Fields Room, Photography Room, Ultrasound Room, Tomography Room, Imaging Room, OCT Laser | EXAM | EXAMINATION | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | -- | 3'-6" | Flush | Wood | _ | _ | 12 S | _ | [10 empty] | 7 |  |  |  | Multilevel Switching, Dimming & Occupancy | Provide dimming and switching to provide various light levels. Provide switching in refraction desk to control overhead lighting. | N/A | 2
8 | Mental Health | QUIET ROOM | Quiet Room for Patients | EXAM | TREATMENT | CPT | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 35 S | [11 empty] | 4 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
8 | Mental Health | BIOFEEDBACK TREATMENT ROOM | Biofeedback Treatment Room | EXAM | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 15 S | [11 empty] | 4 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
9 | Specialty Care Services | PULMONARY FUNCTION ROOM | Pulmonary Function - Analysis | EXAM | TREATMENT | WSF | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 12 G | [11 empty] | 6 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
9 | Specialty Care Services | TREADMILL ROOM | Treadmill Room | EXAM | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 12 MS | [11 empty] | 6 | -- | P9 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
9 | Specialty Care Services | EKG TESTING ROOM | EKG Testing Room | EXAM | EXAMINATION | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0 |  | 3'-6" | Flush | Wood | -- | -- | 12 S | [11 empty] | One per wall | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
9 | Recreation Therapy | GROUP THERAPY ROOM, MUSIC | Creative Arts - Group Therapy Room - Music | -- | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 12 CG | [11 empty] | 8 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
9 | Recreation Therapy | GROUP THERAPY ROOM, ART | Creative Arts - Group Therapy Room - Large | -- | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 12 CG | [11 empty] | 8 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
9 | Recreation Therapy | WEIGHT ROOM, SMALL | Recreation Therapy Exercise / Weight Room - Small | -- | TREATMENT | RF | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 34 AG | [11 empty] | 12 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | --
10 | PHYSICAL THERAPY | PHYSICAL THERAPY GYM | Treatment Exercise Area (includes workstations therapists) | EXAM | TREATMENT | RF | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 14 S | [11 empty] | 14 | -- | P14 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 4
10 | PHYSICAL THERAPY | Activities Daily Living (ADL) Training | ADL Evaluation and Training Center, Toilet, Tub, Bed, Kitchen, Laundry | EXAM | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0 |  | 3'-6" | Flush | Wood | -- | -- | 15 S | [11 empty] | 4 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A
13 | Imaging Services | RADIOLOGY | Radiology, ES: General Purpose Radiology Room | CLASS 1 IMAGING ROOM | TREATMENT | WSF | RB | P | -- | -- | SEE FGI | AT | 9'-0" | 5 | 4'-0" | Flush | Wood | -- | LEAD LINED | 15 LS | 8 | [10 empty] | 5 |  | P3, P13 |  | Fully dimmable, occupancy sensor | N/A | L2 | 2
13 | Imaging Services | C.T. CONTROL ROOM | CT Control Area, X-Ray - Computed Tomography - Control |  | TREATMENT | WSF | WSF | P | -- | -- | SEE FGI | AT | 9'-0" | 5 | 3'-0" | Flush | Wood | -- | LEAD LINED | 12 LS | [8 empty] | 45 |  | M14 | 6 | -- | P3 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 4
13 | Imaging Services | C.T. EQUIPMENT ROOM | CT Equipment Room, X-Ray - Computed Tomography - Indep View Console |  | -- | WSF | WSF | P | -- | -- | -- | AT | 9'-0" | 5 | 6'-0" | Flush | Wood | -- | -- | 45 AG | 7 | [7 empty] | 50 |  | M14 | 7 | -- | P3, P13 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
13 | Imaging Services | C.T. SCAN ROOM | CT Scanning Room (Ceiling Lift), X-Ray - Computed Tomography - Scanner | CLASS 1 IMAGING ROOM | TREATMENT | WSF | WSF | P | -- | -- | SEE FGI | AT | 9'-0" | 5 | 4'-0" | Flush | Wood | -- | LEAD LINED | 15 ALG | [11 empty] | 7 | -- | P3, P13 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
13 | Imaging Services | MAMMOGRAPHY SCAN ROOM | Mammo - X-ray, Mammography Room | CLASS 1 IMAGING ROOM | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | 5 | 3'-6" | Flush | Wood | -- | LEAD LINED | 12 LS | [11 empty] | 7 | -- | P3 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
13 | Imaging Services | RADIOGRAPHIC / FLOURO SCAN ROOM | Radiographic / Fluoroscopic (R/F) Room | CLASS 1 IMAGING ROOM | TREATMENT | WSF | WSF | P | - | - | SEE FGI | AT | 9'-0" | 5 | 3'-6" | Flush | Wood | -- | LEAD LINED | 15 AGL | [11 empty] | 7 | -- | P3, P13 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
13 | Imaging Services | ULTRASOUND SCAN ROOM | Ultrasound Room | CLASS 1 IMAGING ROOM | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 12 S | [11 empty] | 7 | -- | P3, P13 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
13 | Imaging Services | PACS SERVER ROOM | X-Ray - Storage - Digital Files, Viewing Room - Picture Archiving and Communication System (PACS) |  | -- | RFT | RB | P | - | - | - | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | 15 GK | [8 empty] | 50 |  |  | 4 | -- | P3, P13 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 4
13 | Imaging Services | MRI CONTROL ROOM | MRI Control Room, X-Ray - Magnetic Resonance - Control, MRI Zone 3 | CLASS 1 IMAGING ROOM | EXAM - MRI | RFT | RB | P | -- | -- | 40 | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | 12 GS | [8 empty] | 45 |  | M14 | 6 | -- | P3 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 4
13 | Imaging Services | MRI EQUIPMENT ROOM | MRI System Component Room, X-Ray - Magnetic Resonance - System Component |  | TREATMENT | RFT | RB | P | RWC | 4'-0" |  | AT | 9'-0" | 11 | 4'-0" | Flush | Wood | -- | -- | 35 AG |  |  |  |  | 40 |  |  |  | 50 |  | M14 | 7 | -- | P3 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
13 | Imaging Services | MRI FERROMAGNETIC DETECTION | X-Ray - Magnetic Resonance - Ferromagnetic Detection, MRI Zone 2, MRI Viewing Room |  | EXAM - MRI | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" | 2019-11-16 | 4'-0" | Flush | Wood | -- | -- | 15 G |  | 75 | 70 | 60 | 40 | 12 | 2 | Return | 40 | NR |  | 1 | -- | P3 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
13 | Imaging Services | MRI SCAN ROOM | MRI Scanning, X-Ray - Magnetic Resonance - Scanner, |  | EXAM - MRI | WSF | RB | P | -- | -- | SEE FGI | AT | VARIES | 11,13,16 | 4'-0" | Flush | Wood | -- | R/F Shielded | 1 |  | 75 | 70 | 60 | 40 | 12 | 2 | Return Exh. (S) | 50 | NR | M17 | 2 | -- | P3 |  | Multilevel Switching, Dimming & Occupancy | MRI rated fixtures | N/A | 1
13 | Imaging Services | READING ROOM | MRI Viewing Room, X-Ray - Magnetic Resonance - Viewing |  | -- | CPT | RB | P | -- | -- | 40 | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | 12 GS | [8 empty] | 40 |  |  | 6 | -- | P3 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 6
13 | Imaging Services | BONE DENSITOMETRY | Bone Densitometer | EXAM | TREATMENT | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 35 S | [11 empty] | 7 | -- | P3 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
14 | Pathology and Laboratory Medicine | SPECIMEN COLLECTION | Blood Specimen Collection, Alcove - Specimen Collection Point of Care (also for Substance Abuse plus Coumadin), Blood Draw Alcove, Support Area, Laboratory-Satellite, Laboratory-Venipuncture, Blood Draw | EXAM | __ | WSF | WSF | EP | -- | -- | -- | AT | 9'-0" | 3 | -- | _ | _ | _ | _ | _ | 6 | [10 empty] | 4 |  |  |  | Multilevel Switching, Dimming & Occupancy | Multi-level switching or manual dimming | N/A | 2
14 | Pathology and Laboratory Medicine | SPECIMEN ACCESSIONING, PROCESSING & DISTRIBUTION ROOM | Specimen Accessioning, Processing & Distribution Room | LABORATORY WORK ROOM | -- | WSF | WSF | EP | -- | -- | -- | GYP/EP or AT-SP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Wood | Narrow Vision | -- | 15 AG | [11 empty] | One per wall, 6' spacing, one adjacent to sink | One at each workstation |  |  | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | One at each workstation
15 | Pharmacy Service | PHARMACY | Pharmacy, Pharmacy, PACT 3 (Controlled Substance) (w/3 AutoDispensing) | PHARMACY | -- | RF | RB | P | -- | -- | -- | AT | 9'-0" | -- | 6'-0" | Flush | Metal | - | - | 200 AS | 7 | [10 empty] | 15 |  | P5 |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 9
15 | Pharmacy Service | PHARMACY DISPENSING WINDOW | Dispense/Consult Window, Workroom, Pharmacist | PHARMACY | -- | RF | RB | P | -- | -- | -- | AT | 9'-0" | -- | - | - | - | - | - | - | OPEN | [10 empty] | 12 |  |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 5
15 | Pharmacy Service | CLEAN ROOM, COMPOUNDING | Pharmacy - Clean Room - Chemotherapy Compounding | -- | -- | RF | RF | P | -- | -- | -- | GWB:P | 9'-0" | 3 | 7'-0" | Single Slide Auto Sliding Door | Aluminum/ Glass | Yes | -- | 850 |  | 68 | 68 | 60 | 20 | 30 | 2 | Exh. (S) | 55 | (-) | M12 | 14 | -- | P10 |  | Multilevel Switching, Dimming & Occupancy | Sealed fixture, flat lens surface on exterior | N/A | 5
15 | Pharmacy Service | IV ADMIXTURE | Pharmacy - IV Admixture - Low Volume | -- | -- | RF | RF | P | -- | -- | -- | GWB:P | 9'-0" | 3 | 7'-0" | Single Slide Auto Sliding Door | Aluminum/ Glass | Yes | -- | 850 |  | 68 | 68 | 60 | 20 | 30 | 2 | Return | 55 | (++) | M12 | 14 | -- | P10 |  | Multilevel Switching, Dimming & Occupancy | Sealed fixture, flat lens surface on exterior | N/A | 5
15 | Pharmacy Service | PRESCRIPTION DISPENSING AREA | Prescription Dispensing Area - OmniCell Station | -- | -- | RF | RF | P | -- | -- | -- | AT | 9'-0" | 3 | -- | -- | -- | -- | -- | - | 6 | [10 empty] | 8 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 2
15 | Pharmacy Service | SECURE STORAGE VAULT | Secure Storage, Vault | CLEAN WORK ROOM/ CLEAN SUPPLY | -- | RFT | RB | P | RWC | 4'-0" | -- | GWB:P | 9'-0" |  | 3'-0" | Flush | Hollow Metal | -- | -- | 1 | [11 empty] | 1 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | --
15 | Pharmacy Service | ANTEROOM | Anteroom, Compound Sterile Preparation |  | -- | WSF | WSF | EP | -- | -- | -- | GWB:SP | 9'-0" | 3 | 7'-0" | Single Slide Auto Sliding Door | Aluminum/ Glass | Yes | -- | 850 |  | 68 | 68 | 60 | 20 | 30 | 2 | Return | 55 | (+) | M12 | 2 | -- |  |  | Multilevel Switching, Dimming & Occupancy | Sealed fixture, flat lens surface on exterior | N/A | --
17 | Business Office | SECURE CASH ROOM | Secure Money Handling Room |  | -- | RFT | RB | P | -- | -- | -- | AT | 9'-0 |  | 3'-0" | Flush w/ 1-Way Viewer | Steel | -- | -- | 200 GV | [11 empty] | 4 | -- |  |  | Multilevel switching/dimming/occupancy | N/A | N/A | 1
18 | Engineering | BIOMED. REPAIR SHOP | Repair Shop, Biomedical Eng. | -- | -- | RF | RB | P | -- | -- | -- | AT | 9'-0" |  | 3'-6" | Flush | Wood | -- | -- | 35 AG | [7 empty] | Exh. (G) |  | (-) | M7 | 10 | -- | P4, P6 | Surface or chain mounted 1' x 4' | Occupancy/vacancy | N/A | N/A | 2
19 | Logistics | LOADING DOCK | Receiving/ Shipping Dock | -- | -- | CS | RB | EP | -- | -- | -- | EXP. | -- | 8 | 6'-0" | Flush | Wood | -- | -- | 44 APW | 7 | - | 60 | - | - |  |  | Exh. (G) |  | (+) | M5 | 2 | -- |  | Surface or chain mounted 1' x 4' | Occupancy/vacancy | N/A | N/A | 2
19 | Logistics | MAIL ROOM | Support: Mail Room and Dist. Center, Mailing Room - Prosthetic Appliances | -- | -- | RF | RB | P | RWC | 4'-0" | -- | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | 15 G | [11 empty] | 4 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 4
19 | Logistics | GAS CYLINDER STORAGE | Storage - Gas Cylinders - MRI, Storage - Gas Cylinders - Interior | -- | -- | WSF | RB | P | RWC | 4'-0" | -- | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | 45 MIN | 34 G | [7 empty] | Exh. (S) |  | (-) |  | 1 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | --
19 | Logistics | BIO-HAZARD STORAGE | Storage - Bio Hazardous Material, Storage - Hazardous Material, Infectious / Hazardous Waste | REGULATED WASTE | -- | WSF | WSF | EP | RWC | 4'-0" | -- | GWB:SP | 9'-0" | 3 | 3'-6" | Flush | Hollow Metal | -- | -- | 34 G | [11 empty] | 1 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | --
19 | Logistics | STORAGE WAREHOUSE | Bulk Storage, General Storage, Warehouse | CLEAN WORKROOM/CLEAN SUPPLY |  | CS | RB | P | -- | -- | -- | Exp | 10'-0" |  | 6'-0" | Flush | Wood | -- | -- | 45 AG | [11 empty] | minimum, 1 per wall, not to exceed 12' spacing | -- |  | Surface or chain mounted 1' x 4' | Occupancy/vacancy | N/A | N/A
19 | Logistics | BREAK DOWN | Break Down | CLEAN WORKROOM/CLEAN SUPPLY |  | RPT | RB | EP | -- | -- | -- | AT | 9'-0" | 8 | 4'-0" | Flush | Wood | -- | -- | 34 AG | [11 empty] | 1 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A
20 | Police Service | POLICE HOLDING ROOM | Holding Room | -- | -- | CS | RB | P | -- | -- | -- | GWB-PT | 9'-0" | 3,15 | 3'-6" | Flush | Hollow Metal | Half Glass w/ Laminated Glass |  | 18 P | [11 empty] | 0 | -- |  |  | Multilevel Switching, Dimming & Occupancy | Tamperproof fixture design | N/A | --
20 | Police Service | OPERATIONS ROOM | Operations Room |  |  | RFT | RB | P | -- | -- | 40 | AT | 9'-0" |  | 3'-6" | Flush | Hollow Metal | -- | -- | 200 APS | [10 empty] | M15 | 0 | 8 |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 4
20 | Police Service | SECURE STORAGE | Small Arms Armory, Storage - Secure |  |  | RFT | RB | P | -- | -- | -- | AT | 9'-0" |  | 3'-0" | Flush | Hollow Metal | -- | -- | 200 P |  | 75 | 70 | 60 | - | 4 | 2 | Return | NR | NR |  | 1 | -- |  |  | Multilevel Switching, Dimming & Occupancy | N/A | N/A | 1
21 | VCS | RETAIL AREA | Retail Area |  | EXAM - PUBLIC SPACE | RFT | RB | P | -- | -- | SEE FGI | AT | 9'-0 | 17 | 6'-0" | Flush w/ Full Vision | Wood | Full Vision |  | 47 KM | 7, 9 | [9 empty] | M4 | One per wall, 6' spacing | -- |  |  | Multilevel Switching, Dimming & Occupancy | Track or adjustable accent lighting for retail displays. | L5 | 3
23 | OI&T | TELECOMM. | Telecommunications Room/ Closet, IT Telecommunications Room | -- | -- | RFT | RB | P | -- | -- | -- | EXP. | 12'-0" |  | 3'-6" | Flush | Wood | -- | -- | 34 AS |  | 64 | 75 | 55 | 30 | - | - | - | - | NR |  | 6 | -- | P15 | Surface or chain mounted 1' x 4' | Occupancy/vacancy | N/A | N/A | --
23 | OI&T | SERVER ROOM | Central Server Room | -- | -- | RFT | RB | P | -- | -- | -- | EXP. | 12'-0" |  | 3'-6" | Flush | Wood | -- | -- | 34 AS |  | 72 | 81 | 60 | 6 | [5 empty] | M8 | 10 | -- | P15 | Surface or chain mounted 1' x 4' | Occupancy/vacancy | N/A | N/A | --
23 | OI&T | I.T. WORKROOM | IT Workroom, Equip. Configuration/ Repair | -- | -- | RFT | RB | P | -- | -- | -- | AT | 9'-0" |  | 3'-0" | Flush | Wood | -- | -- | 35 AG | [11 empty] | 10 | -- | P4, P6 | Surface or chain mounted 1' x 4' | Occupancy/vacancy | N/A | N/A | 8
24 | SPS | ANTEROOM, SOILED TRANSITION | Anteroom, Soiled Transition/Drop-Off | DECONTAM ROOM | -- | RES | RES | EP | -- | -- | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Steel | Narrow Vision | -- | 15 AG |  | 66 | 72 | 60 | 30 | 10 | 10 | Exhaust (G) | 40 | (-) |  | One per wall | -- |  | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | 2
24 | SPS | DECONTAMINATION ROOM | Decontamination Work Room, Scope Decontamination Room | DECONTAM ROOM | -- | RES | RES | EP |  |  | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Steel | Narrow Vision | -- | 15 AG |  | 66 | 72 | 60 | 30 | 6 | 6 | Exhaust (G) | 40 | (--) |  | One per wall | -- |  | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | 4
24 | SPS | Cart Wash | Cart Wash |  | -- | RES | RES | CT |  |  | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Steel | Narrow Vision | -- | 15 AG |  | 70 | 75 |  |  | 10 | 10 | Exhaust (S) | 40 | (-) | M18, M19 | One per wall | -- |  | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A
24 | SPS | Water Treatment Storage Room | Water Treatment Storage Room |  | -- | RES | RES | EP |  |  | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush | Steel |  | -- | 15 AG |  | 70 | 75 |  |  | 10 | 10 | Exhaust (G) | 40 | (-) | M18, M19 | One per wall | -- |  | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | 1
24 | SPS | REPROCESSING ROOM, SCOPE | Reprocessing Room, Scope |  | -- | RES | RES | EP |  |  | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Steel | Narrow Vision | -- | 15 AG |  | 66 | 72 | 60 | 30 | 6 | 6 | Exhaust (G) | 40 | (-) |  | One per wall | -- |  | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | 2
24 | SPS | Instrument Assembly | Instrument Assembly |  | -- | WSF | WSF | EP |  |  | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Steel | Narrow Vision | -- | 15 AG |  | 66 | 72 | 60 | 30 | 4 | 4 | Exhaust (G) | 40 | (++) |  | One per wall | -- |  | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | 4
24 | SPS | Sterilization Area | Steam Sterilization Area, Low Temp Sterilization Area |  | -- | RES | RES | EP |  |  | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Steel | Narrow Vision | -- | 15 AG |  | 66 | 75 | 60 | 30 | 10 | 10 | Exhaust (G) | 40 | (++) |  | One per wall | -- |  | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | 2
24 | SPS | Cooling Area | Cooling Area |  | -- | RES | RES | EP |  |  | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Steel | Narrow Vision | -- | 15 AG |  | 66 | 75 | 60 | 30 | 10 | 10 | Exhaust (G) | 40 | (++) |  | One per wall | -- |  | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | 1
24 | SPS | Equipment Room, Steam Generator | Equipment Room, Steam Generator |  | -- | RFT | RB | EP |  |  | -- | ACT-SP | 9'-0 | 3, 7 | 3'-6" | Flush | Steel |  | -- | 15 AG |  | 85 |  |  |  | 10 | 10 | Exhaust (G) | 45 | (-) |  | One per wall | -- |  | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | --
24 | SPS | Clean Dispatch | Clean Dispatch |  | -- | RFT | RB | EP |  |  | -- | ACT-SP | 9'-0 | 3, 7 | [7 empty] | 70 | 75 | 60 | 30 | 4 | 4 | Exhaust (G) | 40 |  |  | One per wall | -- |  | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | 1
24 | SPS | STORAGE, CLEAN SCOPE | Storage, Clean Scope | CLEAN SUPPLY | -- | RES | RES | EP | RWC | 4'-0" | -- | GYP-EP | 9'-0 | 3, 7 | 3'-6" | Flush w/ Narrow Vision | Wood | Narrow Vision | -- | 15 AG |  | 66 | 75 | 55 | 30 | 4 |  |  |  | (+) |  | One per wall | -- |  | 2 X 2 recessed lensed | Multilevel Switching, Dimming & Occupancy | Gyp ceiling - lights to be sealed type/flange mounted | N/A | --
Note on L34: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: find out how booths are specified and what is the min requirement for VA.

## Interior Finishes Notes
Interior Finishes Notes
General Notes
A. | Hollow metal frames and doors to be painted.
B. | Window sills to be solid surface fabrication.
C. | Resilient base to be 4", unless otherwise noted.
D. | Provide painted finishes only on inside of exterior walls (no wall covering).
E. | Floor material transitions to occur at centerline of door, unless otherwise noted.
F. | Wall brackets, grills, fire extinguisher cabinets, fin tube radiation, etc. to be painted to match adjacent wall color.
G. | Interior stairwell treads to be concrete with rubber nosings and RFT, LVT or RF landings. Stair nosings to be a contrasting color for safety.
H. | Coordinate height of wall protection with wall-mounted devices.
I. | Gypsum board soffits may be substituted for ACT above locations such as nurse stations, patient transaction/consultation desks, reception desks and
lobby/waiting areas.
J. | Soffit above upper cabinets to be gypsum board.
K. | Refer to FGI recommendations regarding indoor air quality, sustainability and life cycle of materials.
L. | Solid surface countertops to have sides and backsplash at walls.
Schedule Notes
1. | CT tile to 7'-0" on plumbing and adjacent wall(s) with paint above to ceiling.
2. | Tile base to be coved.
3. | Integral coved base 6" high tightly sealed to walls.
4. | If sink is present, use hard suface flooring as noted.
5. | Lead lined walls and control area view window.
6. | Flooring and base to match adjacent area flooring material and base.
7. | Use gasketed, clip down ACT/grid system
8. | Use slip-retardant finish on floor material
9. | Public and exposed open stairways to be treated similar to adjacent spaces using CT/PT/RF on treads. Stair nosings to be a contrasting color for safety.
10. | Note that if wall saver designed chairs are used, no wall protection is required.
11. | Extend all room partitions to structural deck.
12. | CT above countertop on wall.
13. | Ceiling height as required to acommodate equipment.
14. | Cove QT base, 6" high.
15. | No separate trim at top of base, use alternate method to seal to wall.
16. | Ceiling suspension system should be fabricated from nonferromagnetic material.
17. | Aesthetic specialty materials may be used as accents where the design and budget permits.
18. | Ceiling tile to meet USDA regulations.
19. | Floors to be slip-resistant and meet ANSI 326.3 for measuring dynamic coefficient of friction for hard surfaces
20. | Wall base on gyp board but not needed on any exterior materials such as brick, metal, or stone walls.
21. | Wall CT and ceiling to meet building code light reflectancy standards.
22. | Space may be room or area within a room. Coordinate finishes with adjacent spaces.
23. | Provide 3/4" painted plywood where required by Telecommunications.
Finish Codes
AT | Acoustical Ceiling Tile
AT-SP | Acoustical Scrubbable Ceiling Tile (with sprayed plastic finish)
CPT | Carpet Tile
CS | Concrete, Sealed
CT | Ceramic Tile (Wall)
EP | Epoxy Paint
EXP | Exposed Ceiling
MAT | Modular Carpet Walk Off Mat
P | Paint
PT | Porcelain Tile
QT | Quarry Tile
RB | Resilient Base
RES | Resinous Flooring and Base
RF | Rubber Flooring
RFT | Resilient Floor Tile
RSF | Resilient Sheet Flooring - Heterogeneous
RWC | Rigid Wall Covering (Wall Protection)
SD | Static Dissipative Tile
S | Solid Surface Fabrication
WSF | Welded Seam Sheet Flooring - Homogeneous

## Doors and Hardware Notes
Doors and Hardware Notes
General Notes
A. | Refer to Lease Design Narrative (LDN) Appendix for Hardware Groups and Modifiers which are added to numeric hardware group assignments to indicate a variation to
the group.
B. | All doors to be 7'-0" high, unless otherwise noted.
C. | Coordinate acoustical requirements for doors with required wall acoustical ratings as shown in Room Data Matrix - Interior Finishes in Appendix.
Schedule Notes
1. | Hollow metal frame cased opening
2. | Two door (in swing and swing out) acoustical door and frame assembly.
3. | Two doors required at this room/space.
4. | Narrow lite optional. Use insulated or laminated glass to meet acoustical criteria.
5. | Provide STC 50 rated acoustical door.
6. | No door in this room/space.
7. | Equal leaf pair of doors.
8. | Lead lined door and hardware.
9. | Space may be a room or area within another room. Omit door if space is not a separate room.

## Electrical Notes
ELECTRICAL NOTES
POWER NOTES |  | LIGHTING NOTES
P1. | Multiple receptacles above and below desk for device charging, receptacles provided with Pre-Fab system. | L1. | EMI/RFI emissions to be controlled
P2. | Receptacles on all walls | L2. | Dimmable to 5 fc
P3. | Coordinate electrical connections with equipment to be installed. Receptacles on all walls. | L3. | May not have ceiling - then use industrial fixture type
P4. | Plug strip at 44" above counters | L4. | May not have ceiling. If no ceiling, use industrial fixture type
P5. | Multiple receptacles above and below desk for device charging | L5. | Treat like a store. Adjustable lighting, General lighting.
P6. | Cord reel(s) for freestanding workbenches | L6. | No ceiling in these rooms. No prescription for lighting.
P7. | All outlets on dedicated circuits.
P8. | Cord reel(s) for freestanding workbenches
P9. | Treadmill on dedicated circuit
P10. | Each hood on dedicated circuit
P11. | Provide receptacles per equipment plan
P12. | Electrical to review redundancy requirements with OIT guidelines.
P13. | Receptacle above ceiling for overhead lift
P14. | Recessed power quad floor box
P15. | L21-20R receptical above each rack
P16.

## Mechanical Notes
MECHANICAL HVAC NOTES
M1. | Intentioanlly Left Blank
M2. | Per ASHRAE 62 for ventilation, and FGI Guidelines for NC
M3. | General Open Office area
M4. | General Open/Public area
M5. | Per ASHRAE 62 for ventilation if interior enclosed space.
M6. | Comply with ASHRAE 15 if Special Refrigeration Systems are used
M7. | If chemicals are used, provide specialized exhaust
M8. | Data Center
M9. | Transfer air to Food Prep Kitchen
M10. | Intentioanlly Left Blank
M11. | MEP Room
M12. | See USP-797 and -800
M13. | Counter-height specialized exhaust system required
M14. | Provide air conditioning and ventilation per imaging manufacturer recommendations
M15. | General Office Area
M16. | Verify specific vendor/manufacturer requirements.
M17. | Non-ferrous construction
M18. | Provide cooling only air terminal unit to serve the manual equipment wash room.
M19. | Provide a dedicated wet exhaust system