## V A
Appendix B
|  | Security System Application Matrix Department of Veterans Affairs | [17 empty] | 2015-01-01
|  |  |  | (1) |  | (2) |  |  |  | (3) | (4) | (5) |  |  |  | Optional (6)
Area of Coverage |  |  | Fixed Camera | Pan/Tilt/Zoom | Controller | Video Monitor | Local Recording Device | Motion Detection | Glass Break | Door Contact | Card Reader | Biometrics | Intercom | Duress/Panic Alarm | Emergency Phone/Call-Box | X-Ray Machine | WTMD | HHMD | Itemizer
|  |  | VASS |  |  |  |  | IDS |  |  | PACS |  | DSPI |  |  | DSS
BUILDING EXTERIOR
ACCESS ROADWAYS/ VEHICLE GATES |  |  | X | X | [6 empty] | X |  | X
AIR INTAKE AREAS |  |  | X |  |  |  |  | X |  | X
ATM AREAS |  |  | X
CEMETERY
| ADMINISTRATION BUILDINGS (INCLUDES PIC) | [6 empty] | X | X | X | X
COLUMBARIA
COMMITTAL SERVICE SHELTERS
| EXTERIOR WINDOWS (GROUND ACCESSIBLE) | [7 empty] | X
| MAINTENANCE BUILDINGS |  | X |  |  |  | X | X | X | X | X
| MAINTENANCE & STORAGE YARDS |  | X |  |  |  | X | X
PARKING LOT AREAS (EMPLOYEE)
PARKING LOT AREAS (OPEN/VISITOR/VENDOR)
PERIMETER FENCE/WALL/BARRIER
SERVICE ENTRANCE
SERVICE VEHICLE ROADWAY GATES
SERVICE YARDS
VEHICLE ENTRANCE/SITE ACCESS (OPEN ACCESS)
| WATER SUPPLY SYSTEMS (WELLS) |  | X |  |  |  | X
COMMON GROUND/PATHWAYS/SIDEWALKS |  |  | X | X | [10 empty] | X
CREDIT UNION |  |  | X |  |  |  |  | X | X | X |  |  |  | X
CHILD CARE CENTER |  |  | X | X | X | X | X | X | X | X | X |  | X | X | X
DROP OFF / PICK UP POINTS |  |  | X | [11 empty] | X
ELEVATOR MACHINERY ROOM |  |  | X |  |  |  |  | X |  | X | X |  | X
EMERGENCY EXIT/PERIMETER DOORS |  |  | X | X |  |  |  | X |  | X
EMERGENCY ROOM/FACILITY ENTRANCE |  |  | X | X |  |  |  | X | X | X | X |  | X
EMPLOYEE ENTRANCE/SECONDARY DOORS |  |  | X | X |  |  |  | X |  | X | X |  | X
EXTERIOR WINDOWS (AC UNIT INSERTS) |  |  |  | X |  |  |  | X | X
EXTERIOR WINDOWS (GROUND ACCESSIBLE) |  |  |  | X |  |  |  | X | X
HAZARDOUS MATERIAL STORAGE/ENCLOSURES
| BIO HAZARD WASTE |  | X | X |  |  |  | X | X | X | X
| FUEL |  | X | X |  |  |  | X | X | X
| LIQUID OXYGEN |  | X | X |  |  |  | X | X | X
| MEDICAL GAS |  | X | X |  |  |  | X | X | X | X
| PROPANE |  | X | X |  |  |  | X | X | X
| RADIOACTIVE MATERIALS STORAGE |  | X | X |  |  |  | X | X | X | X |  |  | X
| SELECT AGENTS AREA |  | X | X |  |  |  | X | X | X | X |  |  | X
LAUNDRY PLANT |  |  | X | X |  |  |  | X | X | X | X |  | X | X
LOADING DOCKS |  |  | X |  |  | X |  |  |  | X | X |  | X
MAIN ENTRANCE |  |  | X | X |  |  |  |  | X | X |  |  | X
Footnotes:
1 | Pan-Tilt-Zoom cameras shall be deployed primarily to monitor site and building exterior areas. They will supplement the use of fixed cameras if
they can be programmed to monitor multiple areas with minimal human interface required.
2 | A dedicated VASS monitor may be required to provide staff with the ability to monitor access to these controlled areas.
3 | Refer to SDO Matrix for specific door configurations.
4 | Refer to SDO Matrix for PACS configurations. The card credential will be the primary security identity for access control applications.
5 | Biometric security devices shall only be used as a secondary means of identity authentication for an access control application.
6 | The use of DSS equipment is indicated as an optional means to screen persons, items, and materials carried into or delivered to a facility. Each
facility shall be addressed on a case-by-case basis as to DSS equipment requirements.
BUILDING EXTERIOR
MAINTENANCE SHOP |  |  | X | X |  |  |  | X | X | X |  |  |  | X
NURSING HOME |  |  | X | X | X | X | X | X | X | X | X |  | X | X | X
PARKING GARAGES |  |  | X | X | [6 empty] | X |  | X |  | X
PARKING GARAGES (UNDERGROUND) |  |  | X | X | [6 empty] | X |  | X |  | X
PARKING LOT AREAS (EMPLOYEES) |  |  | X | X | [6 empty] | X |  | X |  | X
PARKING LOT AREAS (OPEN/VISITOR/VENDOR) |  |  | X | X | [10 empty] | X
PEDESTRIAN ACCESS POINT |  |  | X | X | [5 empty] | X
PERIMETER FENCE/WALL/BARRIER |  |  | X | X |  |  |  | X
ROOFTOP ACCESS |  |  | X | X |  |  |  | X |  | X | X |  | X
SECURITY GUARD HOUSE/VEHICLE SCREENING AREA |  |  | X | X |  | X |  | X | X |  |  |  | X | X
SERVICE ENTRANCE |  |  | X | X | [5 empty] | X | X |  | X
SERVICE VEHICLE ROADWAY GATES |  |  | X | X | [6 empty] | X |  | X
SERVICE YARD |  |  | X | X | [10 empty] | X
SHIPPING/RECEIVING AREA |  |  | X | X |  |  |  | X | X | X | X |  | X |  |  | X |  |  | X
| LOADING DOCK BAY AREAS |  | X | X |  |  |  | X | X | X | X |  | X | X |  | X |  |  | X
| MAILROOM |  | X | X |  |  |  | X | X | X | X |  | X | X |  | X |  |  | X
UPS BATTERY/GENERATOR AREA |  |  | X | X |  |  |  | X | X | X | X
UTILITY BUILDINGS
| ELECTRICAL |  | X | X |  |  |  | X | X | X | X
| ENERGY CENTER |  | X | X |  |  |  | X | X | X | X |  | X | X
| MECHANICAL |  | X | X |  |  |  | X | X | X | X
| SIGNAL |  | X | X |  |  |  | X | X | X | X
| TELECOMMUNICATIONS |  | X | X |  |  |  | X | X | X | X
| WATER STORAGE / PROCESSING |  | X | X |  |  |  | X | X | X | X
UTILITY SERVICE TUNNEL ENTRANCE/EXIT |  |  | X | X |  |  |  | X |  | X | X |  | X |  | X
VA BENEFITS/REGIONAL OFFICE BUILDING |  |  | X | X |  | X |  | X | X | X | X |  | X | X |  | X | X | X | X
VEHICLE ENTRANCES/SITE ACCESS (OPEN ACCESS) |  |  | X | X | [10 empty] | X
WAREHOUSE BUILDING |  |  | X | X |  | X |  | X | X | X | X |  | X | X |  | X | X | X | X
BUILDING INTERIOR
AGENT CASHIER |  |  | X |  |  |  |  | X | X | X | X |  | X | X
ANIMAL RESEARCH/VIVARIUM |  |  | X |  | X | X |  | X | X | X | X | X | X | X
ATM |  |  | X |  |  |  |  | X | X | X | X
BSL LABS |  |  | X |  | X | X | X | X | X | X | X | X | X | X
BUILDING CORRIDORS (RESTRICTED/CONTROLLED) |  |  | X | X |  |  |  | X | X |  | X |  | X
BUILDING LOBBY/RECEPTION AREA |  |  | X | X |  |  |  |  | X | [6 empty] | X | X | X | X
CAFETERIA |  |  | X |  |  |  |  | X | X | X | X |  |  | X
CANTEEN OFFICE | [7 empty] | X | X | X |  |  |  | X
CANTEEN RETAIL STORE |  |  | X |  |  |  |  | X | X | X |  |  |  | X
CANTEEN STORAGE |  |  | X |  |  |  |  | X | X | X
Footnotes:
1 | Pan-Tilt-Zoom cameras shall be deployed primarily to monitor site and building exterior areas. They will supplement the use of fixed cameras if
they can be programmed to monitor multiple areas with minimal human interface required.
2 | A dedicated VASS monitor may be required to provide staff with the ability to monitor access to these controlled areas.
3 | Refer to SDO Matrix for specific door configurations.
4 | Refer to SDO Matrix for PACS configurations. The card credential will be the primary security identity for access control applications.
5 | Biometric security devices shall only be used as a secondary means of identity authentication for an access control application.
6 | The use of DSS equipment is indicated as an optional means to screen persons, items, and materials carried into or delivered to a facility. Each
facility shall be addressed on a case-by-case basis as to DSS equipment requirements.
BUILDING INTERIOR
CHILD CARE CENTER |  |  | X | X | X | X | X | X | X | X | X |  | X | X | X
COOP ROOM /FACILITY |  |  | X | X | X | X | X | X | X | X | X | X | X
CREDIT UNION |  |  | X |  |  |  |  | X | X | X |  |  |  | X
DOMICILIARY |  |  | X | X |  | X |  | X | X | X | X |  | X | X | X
ELEVATOR EQUIPMENT ROOM |  |  | X |  |  |  |  | X |  | X | X |  |  | X
ELEVATOR LOBBY/FLOOR ACCESS AREAS |  |  | X |  |  |  |  | X | X |  | X |  | X
EMERGENCY EXIT/EGRESS DOORS |  |  | X | X |  |  |  | X |  | X
EMERGENCY (Urgent Care) Area | [10 empty] | X |  | X |  |  | X | X | X | X
| NURSING STATION |  | X | [5 empty] | X |  |  |  |  | X
| WAITING ROOM |  | X | [5 empty] | X
FIRE PUMP ROOM |  |  | X |  |  |  |  | X |  | X | X
GENERAL WAITING AREAS |  |  | X | [5 empty] | X
HAZARDOUS MATERIAL STORAGE/ENCLOSURE
| BIO HAZARD WASTE |  | X | X |  |  |  | X | X | X | X
| FUEL |  | X | X |  |  |  | X | X | X
| LIQUID OXYGEN |  | X | X |  |  |  | X | X | X
| MEDICAL GAS |  | X | X |  |  |  | X | X | X | X
| PROPANE |  | X | X |  |  |  | X | X | X
| RADIOACTIVE MATERIALS STORAGE |  | X |  |  |  |  | X | X | X | X |  |  | X
| SELECT AGENTS AREA |  | X |  |  |  |  | X | X | X | X |  |  | X
INTERSTITIAL SPACE (CONTROLLED ACCESS) |  |  | X | X |  |  |  | X | X | X | X
IRM |  |  | X |  | X | X |  | X | X | X | X | X | X | X
IRM DATA CLOSET |  |  | X | X |  |  |  | X | X | X | X
LABORATORY (CLINICAL) |  |  | X | X | X | X |  | X | X | X | X |  | X | X
LAUNDRY PLANT |  |  | X | X |  |  |  | X | X | X | X |  | X | X
LIBRARY / RESEARCH |  |  | X |  |  |  |  | X | X | X | X |  |  | X
LINEN SUPPLY/STORAGE |  |  | X |  |  |  |  | X | X | X
MAINTENANCE SHOP |  |  | X | X |  |  |  | X | X | X |  |  |  | X
MEDICAL DIRECTORS OFFICE |  |  | X | X |  |  |  | X | X | X | X |  | X | X
MEDICAL GAS BULK STORAGE |  |  | X | X |  |  |  | X | X | X | X
MEDICAL MEDIA EQUIPMENT STORAGE |  |  | X | X |  |  |  | X | X | X | X
MEDICAL RECORDS STORAGE |  |  | X | X |  |  |  | X | X | X | X
NUCLEAR MEDICINE AREAS |  |  | X |  |  |  |  | X | X | X | X |  | X | X
NURSING HOME |  |  | X | X | X | X | X | X | X | X | X |  | X | X | X
OPERATOR SWITCHBOARD |  |  | X | [5 empty] | X | X | X |  | X | X
PEDESTRIAN CORRIDOR |  |  | X | X |  |  |  | X | [6 empty] | X
PEDESTRIAN TUNNEL/ PATHWAYS |  |  | X | X |  |  |  | X | [6 empty] | X
PEDESTRIAN SKYWALK |  |  | X | X |  |  |  | X | [6 empty] | X
Footnotes:
1 | Pan-Tilt-Zoom cameras shall be deployed primarily to monitor site and building exterior areas. They will supplement the use of fixed cameras if
they can be programmed to monitor multiple areas with minimal human interface required.
2 | A dedicated VASS monitor may be required to provide staff with the ability to monitor access to these controlled areas.
3 | Refer to SDO Matrix for specific door configurations.
4 | Refer to SDO Matrix for PACS configurations. The card credential will be the primary security identity for access control applications.
5 | Biometric security devices shall only be used as a secondary means of identity authentication for an access control application.
6 | The use of DSS equipment is indicated as an optional means to screen persons, items, and materials carried into or delivered to a facility. Each
facility shall be addressed on a case-by-case basis as to DSS equipment requirements.
BUILDING INTERIOR
PHARMACY
| CONTROL SUBSTANCE ROOM |  | X |  |  |  |  | X | X | X | X |  | X | X
| DISPENSING ROOM |  | X |  |  |  |  | X | X | X | X |  | X | X
| DRUG CACHE |  | X |  |  |  |  | X | X | X | X |  | X
| DRUG STORAGE ROOM |  | X |  |  |  |  | X | X | X | X |  | X
| INPATIENT/OUTPATIENT SERVICE WINDOWS |  | X |  |  |  |  | X | X |  |  |  |  | X
| MANUFACTURING AREA |  | X |  |  |  |  | X | X | X | X |  |  | X
PRIMARY INVENTORY (MEDICAL SUPPLIES) |  |  | X |  |  |  |  | X | X | X | X
PSYCHIATRIC UNITS |  |  | X |  | X | X |  |  | X | X | X |  | X | X
RESEARCH CLINICAL LABS |  |  | X |  | X | X |  | X | X | X | X |  | X | X
RESEARCH LIBRARY |  |  | X |  | X | X |  | X | X | X | X |  | X | X
SECURITY CONTROL CENTER (SCC) |  |  | X |  | X | X | X |  | X | X | X |  | X | X
SECURITY SYSTEM EQUIPMENT CLOSETS |  |  | X |  |  |  |  | X | X | X | X
SHIPPING/RECEIVING AREA
| LOADING DOCK BAY AREAS |  | X | X |  |  |  | X | X | X | X |  | X | X |  | X |  |  | X
| MAILROOM |  | X |  |  |  |  | X | X | X | X |  |  | X |  | X |  |  | X
STAIRWELLS |  |  | X |  |  |  |  | X | X | X | X |  | X |  | X
TELECOMMUNICATION/DATA EQUIPMENT AREAS
| TELEPHONE DATA CLOSET |  | X |  |  |  |  | X | X | X | X |  | X
| MAIN COMPUTER ROOM |  | X |  |  |  |  | X | X | X | X |  | X
| MAIN TELEPHONE ROOM |  | X |  |  |  |  | X | X | X | X |  | X
TRAVEL OFFICE |  |  | X |  |  |  |  | X | X | X | X |  |  | X
UTILITY ROOMS
BATTERY-UPS-GENERATOR AREA |  |  | X |  |  |  |  | X | X | X | X |  | X
ELECTRICAL |  |  | X |  |  |  |  | X | X | X | X |  | X
MECHANICAL |  |  | X |  |  |  |  | X | X | X | X |  | X
SIGNAL |  |  | X |  |  |  |  | X | X | X | X |  | X
TELECOMMUNICATIONS |  |  | X |  |  |  |  | X | X | X | X |  | X
UTILITY TUNNEL PATHWAY |  |  | X | X |  |  |  | X |  | X | X |  |  |  | X
VA BENEFITS/REGIONAL OFFICE BUILDING |  |  | X | X |  |  |  | X | X | X | X |  | X | X |  | X | X | X | X
VA POLICE OFFICE
| HOLDING AREA |  | X |  | X | X | X |  | X | X | X |  | X
| PROCESSING ROOM | [6 empty] | X | X | X | X
| PROPERTY/EVIDENCE ROOM |  | X |  |  |  |  | X | X | X | X
| WEAPON STORAGE/ARMORY |  | X |  | X | X | X | X | X | X | X
WARD/MEDICAL TREATMENT ROOMS |  |  | X |  |  |  |  | X | X | X | X |  | X | X
Footnotes:
1 | Pan-Tilt-Zoom cameras shall be deployed primarily to monitor site and building exterior areas. They will supplement the use of fixed cameras if
they can be programmed to monitor multiple areas with minimal human interface required.
2 | A dedicated VASS monitor may be required to provide staff with the ability to monitor access to these controlled areas.
3 | Refer to SDO Matrix for specific door configurations.
4 | Refer to SDO Matrix for PACS configurations. The card credential will be the primary security identity for access control applications.
5 | Biometric security devices shall only be used as a secondary means of identity authentication for an access control application.
6 | The use of DSS equipment is indicated as an optional means to screen persons, items, and materials carried into or delivered to a facility. Each
facility shall be addressed on a case-by-case basis as to DSS equipment requirements.