## scanarios
2016-05-01
VA DIALYSIS DEPLOYMENT PACKAGE SCENARIOS
|  |  | 12 |  |  | 16 |  |  | 20 |  |  | 24 |  |  | 28 |  |  | 32 |  |  | 36 |  |  | COMMENTS
|  |  | Q | NSF | TOT | Q | NSF | TOT | Q | NSF | TOT | Q | NSF | TOT | Q | NSF | TOT | Q | NSF | TOT | Q | NSF | TOT |  | 1 | 2 | 3 | 4 | 5 | 6 | 7
| RECEPTION AREA | [23 empty] | 12 | 16 | 20 | 24 | 28 | 32 | 36
| 1 | Waiting | 1 | 240 | 240 | 1 | 240 | 240 | 1 | 280 | 280 | 1 | 280 | 280 | 1 | 280 | 280 | 1 | 320 | 320 | 1 | 320 | 320 | FGI Guidelines 2014: 3.10-6.1 Public Areas The following public areas shall be available or accessible to the dialysis center: *3.10-6.1.1 A waiting room 3.10-6.1.2 Toilet room with hand-washing stations 3.10-6.1.3 Provisions for drinking water 3.10-6.1.4 Access to make local phone calls 3.10-6.1.5 Seating accommodations for waiting periods | 20 | 15 | 14 | 11.6667 | 10 | 10 | 8.8889
| 2 | Reception | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | NSF provides space for receptionist as well as business supplies and machines. On 10/3: Changed sizes of 20 - 36 to be 120 NSF. | 10 | 7.5 | 6 | 5 | 4.2857 | 3.75 | 3.3333
| 3 | Toilet, Public | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 |  | 5 | 3.75 | 3 | 2.5 | 2.1429 | 1.875 | 1.6667
| 4 | Alcove, Patient Personal Property Lockers | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 80 | 80 | 1 | 80 | 80 | 1 | 80 | 80 | 1 | 100 | 100 | 1 | 100 | 100 | Two lockers per station. Need to validate. | 5 | 3.75 | 4 | 3.3333 | 2.8571 | 3.125 | 2.7778
PATIENT AREA
| 5 | Renal Dialysis, Chair Station | 10 | 80 | 800 | 14 | 80 | 1120 | 17 | 80 | 1360 | 21 | 80 | 1680 | 25 | 80 | 2000 | 28 | 80 | 2240 | 32 | 80 | 2560 | FGI 2014: 3.10-3.2.2.1 Individual patient treatment areas shall contain at least 80 square feet. *3.10-3.2.2.2 There shall be have a clear dimension of at least 4 feet between beds and/or dialysis chairs. | 66.6667 | 70 | 68 | 70 | 71.4286 | 70 | 71.1111
| 6 | Renal Dialysis, Bariatric Chair Station | 2 | 100 | 200 | 2 | 100 | 200 | 3 | 100 | 300 | 3 | 100 | 300 | 3 | 100 | 300 | 4 | 100 | 400 | 4 | 100 | 400 | NSF acccommodates space for bariatric dialysis treatment chair. Space is able to flex as space for a stretcher. This space will be outfitted with a ceiling lift. | 16.6667 | 12.5 | 15 | 12.5 | 10.7143 | 12.5 | 11.1111
| 7 | Renal Dialysis,Separation Room | 1 | 140 | 140 | 1 | 140 | 140 | 1 | 140 | 140 | 1 | 140 | 140 | 1 | 140 | 140 | 1 | 140 | 140 | 1 | 140 | 140 | NSF provides space for a private room to hemodialyze patients who are hepatitis B ssurface antigen-positive. This space is flexible to accommodate a stretcher. It has a handwashing station. Allows for direct observation of the patient by staff during treatment via a sliding glass door. (Not airborne infection isolation room (AIIR) -FGI does not require an AIIR --only per ICRA). This room could accommodate a patient who might agitate or cause anxiety for other patients. HDR Test Fit was 144 NSF for this room. VA SPC Chapter is 150 NSF. FGI Guidelines: 2014: *3.10-3.4.2 Separation Area: Facilities that hemodialyze patients who are hepatitis B surface antigen-positive shall have at least one separate area with walls that have a minimum height of 5 feet (xx meters) for hemodialysis treatment of those pts. 3.10-3.4.2.1 Space requirements: The separation area shall have a minimum clear floor area of 120 square feet. 3.10-3.4.2.2 The separation area shall contain a hand-washing station. 3.10-3.4.2.3 The separation area shall allow for direct observation of the patient by staff during treatment. | 11.6667 | 8.75 | 7 | 5.8333 | 5 | 4.375 | 3.8889
| 8 | Toilet, Separation Room Patient | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | Dedicated toilet for the Renal Dialysis Separation Room. | 5 | 3.75 | 3 | 2.5 | 2.1429 | 1.875 | 1.6667
| 9 | Home Training Room | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | A private training room provided for patients who are being trained to perform home peritoneal dialysis and home hemodialysis. It will be plumbed for hemodialysis and includes a counter, hand-washing station, purified water, a separate drain for fluid disposal. FGI Guidelines 2014: 3.10-3.3 Home Training Room. If home training is provided at the center, the following requirements shall be met: 3.10-3.3.1 A private treatment area of at least 120 square feet (11.15 square meters) shall be provided for patients who are being trained to use dialysis equipment at home. 3.10-3.3.2 This room shall contain a counter, hand-washing stations, and a separate drain for fluid disposal. | 10 | 7.5 | 6 | 5 | 4.2857 | 3.75 | 3.3333
| 10 | Nurse Station / Workarea | 2 | 120 | 240 | 2 | 185 | 370 | 4 | 125 | 500 | 4 | 115 | 460 | 4 | 190 | 760 | 8 | 90 | 720 | 6 | 120 | 720 | 1NSF provides space for nurse workstations and work area for staff. 10/23: For 24 and 28 station scenarios, need to divide total NSF into 2 Nurse Stations. FGI 2014 Guidelines 3.10-3.2.8 Nurse Station (s) shall be located within the dialysis treatment area and designed to provide visual observation of all patient stations. CMS: 494.60(c)(4), ‘‘Patients must be in view of staff during hemodialysis treatment to ensure patient safety (video surveillance will not meet this requirement).’’ | [6 empty] | 20
| 12 | Workstation, Decentralized | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | 0 | 30 | 0 | NSF provides space for a computer workstation for every 4 dialysis treatment stations. 10/23 Added one workstation to improve visualization of dialysis stations. | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 13 | Nourishment Station | 1 | 40 | 40 | 1 | 40 | 40 | 1 | 40 | 40 | 1 | 40 | 40 | 1 | 40 | 40 | 1 | 40 | 40 | 1 | 40 | 40 | Space provided for a nourishment room, center or area with staff access only, serving patient's needs. Storage and preparation area for ice chips, beverages and snacks. | 3.3333 | 2.5 | 2 | 1.6667 | 1.4286 | 1.25 | 1.1111
| 14 | Exam Room | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | This room is used for physical exams prior to treatment; to implant cannulas; to remove clots from shunts; and to perform special examinations, treatment. FGI 2014 Guidelines: 3.10-3.1 At least one examination room shall be provided. 3.10-3.1.1 The examination room shall have a minimum clear floor area of 100 square feet (9.29 square meters). 3.10-3.1.2 The examination room shall have the following: 3.10-3.1.2.1 Hand-washing station 3.10-3.1.2.2 A counter or shelf space for writing or electronic documentation. | 10 | 7.5 | 6 | 5 | 4.2857 | 3.75 | 3.3333
| 15 | Toilet, Patient | 1 | 75 | 75 | 1 | 75 | 75 | 1 | 75 | 75 | 1 | 75 | 75 | 1 | 75 | 75 | 1 | 75 | 75 | 2 | 75 | 150 | This patient toilet is sized to accommodate the bariatric patient | 6.25 | 4.6875 | 3.75 | 3.125 | 2.6786 | 2.3438 | 4.1667
| 16 | Toilet, Patient | 0 | 60 | 0 | 0 | 60 | 0 | 0 | 60 | 0 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60
| 17 | In-Floor Scale | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | Recessed floor scale for weighing patients who are non-ambulatory, bariatric, in wheelchairs. | 5 | 3.75 | 3 | 2.5 | 2.1429 | 1.875 | 1.6667
| 18 | Alcove, Wheelchair | 1 | 60 | 60 | 1 | 75 | 75 | 1 | 90 | 90 | 1 | 105 | 105 | 1 | 120 | 120 | 1 | 135 | 135 | 1 | 150 | 150 | Provides space for wheelchairs and personal scooters at a ratio of one wheelchair storage space per every four dialysis stations. FGI 2014 Guidelines: 3.10-3.6.11.3 Wheelchair storage space shall be provided as indicated in Section 3.1-3.6.11.3 at a ratio of not less than one wheelchair storage space for each four stations. | 5 | 4.6875 | 4.5 | 4.375 | 4.2857 | 4.2188 | 4.1667
| 19 | Alcove, Quick Response Cart | 1 | 20 | 20 | 1 | 20 | 20 | 1 | 20 | 20 | 2 | 20 | 40 | 2 | 20 | 40 | 2 | 20 | 40 | 3 | 20 | 60 | NSF provides space to store emergency kits / cart.
| 20 | Alcove, Portable Lift | 1 | 20 | 20 | 1 | 20 | 20 | 1 | 20 | 20 | 1 | 20 | 20 | 1 | 20 | 20 | 1 | 20 | 20 | 1 | 20 | 20 | NSF provides space to store one portable lift. This space may be combined with the equipment room. | 1.6667 | 1.25 | 1 | 0.83333 | 0.71429 | 0.625 | 0.55556
| 21 | Alcove, Mobile Equipment | 1 | 20 | 20 | 1 | 20 | 20 | 2 | 20 | 40 | 2 | 20 | 40 | 2 | 20 | 40 | 2 | 20 | 40 | 3 | 20 | 60
SUPPORT AREA
| 22 | Dialysate Preparation Room | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 10/9/2013: Deleted this room and combined with Water Treatment Room. 10/3/2013: Need to validate whether this room will be separate or combined with the Water Treatment Room. Need to validate VA Policy as to need for this room. NSF provides space to prepare special dialysis solutions for a patient. Includes space for dialysate mixing and distribution equipment. FGI 2014: 3.10-5.1.2 Dialysate Solutions Preparation Room. 3.10-5.1.2.1 Each facility using a central batch delivery system shall provide, either on the premises or through written arrangements, individual delivery systems for the treatment of any patient requiring special dialysis solutions. 3.10-5.1.2.2 A dialysate preparation area with sufficient space to accommodate the dialysate mixing and distribution equipment shall be provided. It shall include the following: (1) A sink, (2) Storage space, and (3) Holding tanks, (4) Floor drain
| 23 | Water Treatment / Dialysate Prep. Room | 1 | 345 | 345 | 1 | 345 | 345 | 1 | 345 | 345 | 1 | 345 | 345 | 1 | 345 | 345 | 1 | 440 | 440 | 1 | 440 | 440 | NSF accommodates space for dialsysate preparation. | 28.75 | 21.5625 | 17.25 | 14.375 | 12.3214 | 13.75 | 12.2222
| 24 | Water Heater Room | 1 | 40 | 40 | 1 | 40 | 40 | 1 | 40 | 40 | 1 | 40 | 40 | 1 | 40 | 40 | 1 | 40 | 40 | 1 | 40 | 40
| 25 | Medication Preparation Room | 1 | 80 | 80 | 1 | 80 | 80 | 1 | 90 | 90 | 1 | 90 | 90 | 1 | 90 | 90 | 1 | 100 | 100 | 1 | 100 | 100 | FGI 2014: 3.10-3.6.6 Medication Station If required by the functional program, there shall be a medication dispensing station for the dialysis center. 3.10-3.6.6.1 A work counter and hand-washing stations shall be included in this area. 3.10-3.6.6.2 Provisions shall be made for the controlled storage, preparation, distribution, and refrigeration of medications | 6.6667 | 5 | 4.5 | 3.75 | 3.2143 | 3.125 | 2.7778
| 26 | Laboratory, Biochemistry | 1 | 80 | 80 | 1 | 80 | 80 | 1 | 90 | 90 | 1 | 90 | 90 | 1 | 90 | 90 | 1 | 100 | 100 | 1 | 100 | 100 | Provides space for a lab testing room. Space should include tech workstation, countertop space, handwashing sink, under counter refrigerator and data drops.
| 27 | Biomed Engineering | 1 | 150 | 150 | 1 | 150 | 150 | 1 | 150 | 150 | 1 | 150 | 150 | 1 | 180 | 180 | 1 | 180 | 180 | 1 | 180 | 180 | FGI 2014: *3.10-5.1.3 Equipment Repair Room. An equipment repair and breakdown room shall be provided and equipped with the following: 3.10-5.1.3.1 A hand-washing station 3.10-5.1.3.2 Product water for preparation of dialysate supply and drain for equipment connection and testing or a deep service sink 3.10-5.1.3.3 A counter, table, or area for a desk to serve as designated documentation space 3.10-5.1.3.4 Storage for supplies, tools, parts, and records
| 28 | Utility Room, Soiled | 1 | 80 | 80 | 1 | 80 | 80 | 1 | 90 | 90 | 1 | 90 | 90 | 1 | 90 | 90 | 1 | 100 | 100 | 1 | 100 | 100 | FGI 2014: 3.10-3.6.10 Soiled Workroom or Soiled Holding Room A soiled workroom shall be provided and shall contain the following: 3.10-3.6.10.1 Soiled workroom. If a soiled workroom is provided, it shall contain the following: A flushing-rim sink. a hand-washing station, a work counter, storage cabinets, waste receptacles, a soiled linen receptacle. 3.10-3.6.10.2 Soiled holding room. A waste storage room with a minimum area of 50 square feet shall be provided
| 29 | Utility Room, Clean | 1 | 100 | 100 | 1 | 100 | 100 | 1 | 110 | 110 | 1 | 110 | 110 | 1 | 110 | 110 | 1 | 120 | 120 | 1 | 120 | 120 | NSF provides space for one week's supply of disposable and non-sterile supplies such as, but not limited to: dialysate acid concentrate, dialysate bicarbonate, vinegar, bleach, dialyzers, blood lines, and plastic aprons. NSF also provides space for clean linens. FGI Guidelines: 2014: 3.10-3.6.9 Clean Workroom or Clean Supply Room A clean workroom and/or clean supply room shall be provided. Such rooms shall be separated from the soiled workroom and have no direct connection to it. If the room is used only for storage and holding as part of a system for distribution of clean and sterile materials, omission of the work counter and hand-washing station shall be permitted. FGI 2014: 3.10-3.6.11 Equipment and Supply Storage 3.10-3.6.11.1 Clean linen storage. If blankets or other linens are used, a clean linen storage area shall be provided. (1) Location of the clean linen storage area within the clean workroom, a separate closet, or an approved distribution system shall be permitted.
| 30 | Storage, Equipment | 1 | 150 | 150 | 1 | 150 | 150 | 1 | 180 | 180 | 1 | 180 | 180 | 1 | 180 | 180 | 1 | 210 | 210 | 1 | 210 | 210 | NSF provides space for extra dialysis machines. Provide one extra dialysis machine for every four dialysis treatment stations. (2) If a closed cart system is used, storage in an alcove shall be permitted. It must be out of the path of normal traffic and under staff control.3.10-3.6.11.2 Equipment supply facilities. Supply areas or supply carts shall be provided.
| 31 | Storage, Supplies | 1 | 300 | 300 | 1 | 300 | 300 | 1 | 400 | 400 | 1 | 400 | 400 | 1 | 500 | 500 | 1 | 500 | 500 | 1 | 600 | 600 | Include separate space in this room for peritoneal dialysis supplies. 10/24: Increased size of supply room per Dr. Kourany and Dr. Crowley.
| 32 | Communications Closet | 1 | 100 | 100 | 1 | 100 | 100 | 1 | 100 | 100 | 1 | 100 | 100 | 1 | 100 | 100 | 1 | 100 | 100 | 1 | 100 | 100 | Engineers to verify room NSF
| 33 | Electrical Closet | 1 | 100 | 100 | 1 | 100 | 100 | 1 | 100 | 100 | 1 | 100 | 100 | 1 | 100 | 100 | 1 | 100 | 100 | 1 | 100 | 100 | Engineers to verify room NSF
| 34 | Housekeeping Aids Closet -- HAC | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 3.10-3.6.12 Environmental Services Room An environmental services room shall be provided in accordance with Section 3.1-5.5.1.
STAFF & ADMINISTRATIVE AREA
| 35 | Office, Physician | 1 | 140 | 140 | 1 | 140 | 140 | 1 | 140 | 140 | 1 | 140 | 140 | 1 | 140 | 140 | 1 | 140 | 140 | 1 | 140 | 140 | 10/3: Increased size to 140 NSF.
| 36 | Office, Physician | 0 | 120 | 0 | 0 | 120 | 0 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120
| 37 | Office, Nurse Manager | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120
| 38 | Office, Dietitian | 0 | 120 | 0 | 0 | 120 | 0 | 0 | 120 | 0 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120
| 39 | Office, Social Worker | 0 | 120 | 0 | 0 | 120 | 0 | 0 | 120 | 0 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120 | 1 | 120 | 120
| 40 | Office, Shared | 1 | 140 | 140 | 1 | 140 | 140 | 1 | 140 | 140 | 0 | 140 | 0 | 0 | 140 | 0 | 0 | 140 | 0 | 0 | 140 | 0 | For 12, 16 and 20 dialysis chair stations, the shared office and consultation room is for the social worker and dietitian. In the 32 and 36 chair station scenario, the shared office is for two social workers. 10/3: Decreased size from 180 to 140 NSF.
| 41 | Classroom / Conference Room | 1 | 225 | 225 | 1 | 225 | 225 | 1 | 300 | 300 | 1 | 300 | 300 | 1 | 300 | 300 | 1 | 300 | 300 | 1 | 300 | 300 | NSF provides space for staff and family conferences, patient and staff training. CMS: Staff training requirements (§ 494.60(d)(1)) state that the dialysis facility must ‘‘provide appropriate training and orientation in emergency preparedness to the staff. Staff training must be provided and evaluated at least annually. Patient Training: E.g.Continuous Ambulatory Peritoneal Dialysis (CAPD). Continuous Cycling Peritoneal Dialysis (CCPD). All dialysis patients, whether home or in-center, are to receive counseling regarding nutrition and psychosocial well-being
| 43 | Locker / Changing Room, Male | 0 | 80 | 0 | 0 | 80 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 120 | 0 | 0 | 120 | 0 | The male and female locker / changing rooms may be combined per make up of local staffing
| 44 | Locker / Changing Room, Female | 0 | 80 | 0 | 0 | 80 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 100 | 0 | 0 | 120 | 0 | 0 | 120 | 0 | The male and female locker / changing rooms may be combined per make up of local staffing
| 45 | Lockers, Staff | 1 | 45 | 45 | 1 | 45 | 45 | 1 | 50 | 50 | 1 | 50 | 50 | 1 | 50 | 50 | 1 | 55 | 55 | 1 | 55 | 55 | 10/3: Staff will share the Locker/Changing Room for 12, 16 and 20 Station Center.
| 46 | Lounge, Staff / Locker Room | 1 | 165 | 165 | 1 | 165 | 165 | 1 | 190 | 190 | 1 | 190 | 190 | 1 | 190 | 190 | 1 | 220 | 220 | 1 | 220 | 220
| 46 | Toilet, Staff | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 1 | 60 | 60 | 2 | 60 | 120 | 2 | 60 | 120 | 2 | 60 | 120
| NSF Subtotal |  | 4935 |  |  | 5400 |  |  | 6360 |  |  | 6835 |  |  | 7660 |  |  | 8235 |  |  | 8785
| 1.5 |  | 2467.5 |  |  | 2700 |  |  | 3180 |  |  | 3417.5 |  |  | 3830 |  |  | 4117.5 |  |  | 4392.5
| Net Usable Square Feet (NUSF) |  | 7402.5 |  |  | 8100 |  |  | 9540 |  |  | 10252.5 |  |  | 11490 |  |  | 12352.5 |  |  | 13177.5
| NUSF/Chair |  | 616.875 |  |  | 506.25 |  |  | 477 |  |  | 427.1875 |  |  | 410.3571 |  |  | 386.0156 |  |  | 366.0417
| NSF/Chair | NSF/Chair | 411.25 |  |  | 337.5 |  |  | 318 |  |  | 284.7917 |  |  | 273.5714 |  |  | 257.3438 |  |  | 244.0278
3.10-1.3 Site
The location of a renal dialysis facility shall offer access from parking and from public transportation, if available.
3.10-3.2 Dialysis Treatment Area
3.10-3.2.1 General
3.10-3.2.1.1 Layout
(1) The treatment area shall be separate from administrative and waiting areas.
(2) The treatment area shall be permitted to be an open area.
(3) Open treatment areas shall be designed to provide privacy for each patient
3.10-3.2.5 Hand-Washing Station
Hand-washing stations shall be provided following the requirements of Section 3.1-7.2.2.8 3.1-3.6.5.
(1) A hand-washing station shall be located at the entry to the hemodialysis treatment area. (This handwashing
station shall be permitted to contribute to the total number of hand-washing stations
required.)
(2) A hand-washing station shall be provided for each four individual treatment bays and each fraction
thereof.
(3) A hand-washing station shall be no more than 15 feet from each patient station.
3.10-8 Building Systems
3.10-8.2 Heating, Ventilating, and Air-Conditioning (HVAC) Systems
For requirements, see 3.1-8.2.
*3.10-8.2.1 Dialyzer Reprocessing Room Ventilation Requirements
Ventilation for this room shall comply with the requirements for endoscopic instrument processing rooms
in Part 6 (ANSI/ASHRAE/ASHE 170: Ventilation of Health Care Facilities). Table 2.1-2 (Ventilation
Requirements for Areas Affecting Patient Care in Hospitals and Outpatient Facilities).
3.10-8.3 Reserved Electrical Systems
For requirements, see 3.1-8.3.
3.10-8.4 Plumbing Systems
For requirements, see 3.1-8.4.
*3.10-8.4.1 Plumbing and Other Piping Systems
3.10-8.4.1.1 Design consideration shall be given to the disposal of The liquid waste and disposal system
for the hemodialysis treatment area shall be designed to from the dialyzing process to prevent minimize
odor and prevent backflow.
3.10-8.4.1.2 Hemodialysis water distribution
(1) A separate treated, purified water distribution system
and a drainage system that is independent from the tap water and
hand-washing system shall be provided.
CMS: Separate dedicated supplies and equipment must be used to provide care to the HBsAg-positive patient. Note that ‘‘separate equipment’’ includes glucometers. Use of an ‘‘end of row’’ hemodialysis station can facilitate the separation of the area from the mainstream of the dialysis facility’s activities and decreases the number of adjacent dialysis stations. If this space is needed for both HBsAg-positive as well as HBsAg-negative patients on other shifts, the space may be disinfected using conventional protocols and used for both types of patients at different times. If a facility does not have any HBsAg-positive patients, this space may be used by non-HBsAg-positive patients on a normal basis. Every facility must have the capacity to separate HBsAg-positive patients in the facility. The CDC infection control precautions specifically call for separate staff to care for hepatitis B-positive patients to prevent infection of susceptible dialysis patients.