SECTION 27 10 00  
CONTROL, COMMUNICATION AND SIGNAL WIRING

SPEC WRITER NOTES:

1. Edit this specification section between //\_\_\_\_//, to fit project, or delete if not applicable.

2. Contact VA’s AHJ, Spectrum Management and COMSEC Service (SMCS 005OP2H3), (202-461-5310), for all technical assistance.

3. Included throughout this specification are references to system’s interface capability and various related features. System designer must verify availability of this system and coordinate associated requirements and subsequent interfaces.

1. GENERAL
   1. DESCRIPTION
      1. This section includes control, communication and signal wiring for a comprehensive systems infrastructure.
      2. This section applies to all sections of Divisions 27 // and 28 //.
   2. RELATED WORK
      1. Excavation and backfill for cables that are installed in conduit: Section 31 20 00, EARTH MOVING.
      2. Sealing around penetrations to maintain integrity of time rated construction: Section 07 84 00, FIRESTOPPING.
      3. General electrical requirements that are common to more than one section in Division 27: Section 27 05 11, REQUIREMENTS FOR COMMUNICATIONS INSTALLATIONS.
      4. Conduits for cables and wiring: Section 27 05 33, RACEWAYS AND BOXES FOR COMMUNICATIONS SYSTEMS.
      5. Requirements for personnel safety and to provide a low impedance path for possible ground fault currents: Section 27 05 26, GROUNDING AND BONDING FOR COMMUNICATIONS SYSTEMS.
   3. SUBMITTALS
      1. Submit in accordance with Section 27 05 11, REQUIREMENTS FOR COMMUNICATIONS INSTALLATIONS.
      2. Submit written certification from OEM:
         1. Indicate wiring and connection diagrams meet National and Government Life Safety Guidelines, NFPA, NEC, NRTL, Joint Commission, OEM, this section and Section 27 05 11, REQUIREMENTS FOR COMMUNICATIONS INSTALLATIONS.
         2. Include instructions, requirements, recommendations, and guidance for proper performance of system as described herein.
         3. Government will not approve any submittal without this certification.
      3. Identify environmental specifications on technical submittals; identify requirements for installation.
         1. Minimum floor space and ceiling heights.
         2. Minimum size of doors for cable reel passage.
      4. Power: Provide specific voltage, amperage, phases, // generator equipment // and quantities of circuits.
      5. Provide conduit size requirements.
      6. Closeout Submittals:
         1. Provide contact information for maintenance personnel to contact contractor for emergency maintenance and logistic assistance, and assistance in resolving technical problems at any time during warranty period.
         2. Provide certified OEM sweep test tags from each cable reel to COR.
         3. Furnish spare or unused wire and cable with appropriate connectors (female types) for installation in appropriate punch blocks, barrier strips, patch, or bulkhead connector panels.
         4. Turn over unused and opened installation kit boxes, coaxial, fiber optic, and twisted pair cable reels, conduit, cable tray, cable duct bundles, wire rolls, physical installation hardware to COR.
         5. Documentation: Include any item or quantity of items, as installed drawings, equipment, maintenance, and operation manuals, and OEM materials needed to completely and correctly provide system documentation required herein.
2. PRODUCTS
   1. CONTROL WIRING
      1. Provide control wiring large enough so voltage drop under in-rush conditions does not adversely affect operation of controls.
      2. Provide cable meeting specifications for type of cable.
      3. Outside Location (i.e. above ground, underground in conduit, ducts, pathways, etc.): Provide cables filled with a waterproofing compound between outside jacket (not touching any provided armor) and inter conductors to seal punctures in jacket and protect conductors from moisture.
      4. Remote Control Cable:
         1. Multi-conductor with stranded conductors able to handle power and voltage required to control specified system equipment, from a remote location.
         2. NRTL listed and pass VW-1 vertical wire flame test (UL 83) (formerly FR-1).
         3. Color-coded Conductors: Combined multi-conductor and coaxial cables are acceptable for this installation, on condition system performance standards are met.
         4. Technical Characteristics:
            1. Length: As required, in 1K (3,000 ft.) reels minimum.
            2. Connectors: As required by system design.
            3. Size:

18 AWG, minimum, Outside.

20 AWG, minimum, Inside.

* + - * 1. Color Coding: Required, EIA industry standard.
        2. Bend Radius: 10 times cable outside diameter.
        3. Impedance: As required.
        4. Shield Coverage: As required by OEM specification.
        5. Attenuation:

|  |  |
| --- | --- |
| Frequency in MHz | dB per 305 Meter (1,000 feet), maximum |
| 0.7 | 5.2 |
| 1.0 | 6.5 |
| 4.0 | 14.0 |
| 8.0 | 19.0 |
| 16.0 | 26.0 |
| 20.0 | 29.0 |
| 25.0 | 33.0 |
| 31.0 | 36.0 |
| 50.0 | 52.0 |

* + 1. Distribution System Signal Wires and Cables:
       1. Provide in same manner, and use construction practices, as Fire Protective and other Emergency Systems identified and defined in NFPA 101, Life Safety Code, Chapters 7, 12, and 13, NFPA 70, National Electrical Code, Chapter 7, Special Conditions.
       2. Provide system able to withstand adverse environmental conditions without deterioration, in their respective location.
       3. Provide entering of each equipment enclosure, console, cabinet or rack in such a manner that all doors or access panels can be opened and closed without removal or disruption of cables.
       4. Terminate on an item of equipment by direct connection.
  1. COMMUNICATION AND SIGNAL WIRING
     1. Provide communications and signal wiring conforming to recommendations of manufacturers of systems // ; provide not less than TIA Performance Category 5e // .
     2. Wiring shown is for typical systems; provide wiring as required for systems being provided.
     3. Provide color-coded conductor insulation for multi-conductor cables.
     4. Connectors:
        1. Provide connectors for transmission lines, and signal extensions to maintain uninterupted continuity, ensure effective connection, and preserve uniform polarity between all points in system.
           1. Provide AC barrier strips with a protective cover to prevent accidental contact with wires carrying live AC current.
           2. Provide punch blocks for signal connection, not AC power. AC power twist-on wire connectors are not permitted for signal wire terminations.
        2. Cables: Provide connectors designed for specific size cable and conductors being installed with OEM's approved installation tool. Typical system cable connectors include:
           1. Audio spade lug.
           2. Punch block.
           3. Wirewrap.
  2. INSTALLATION KIT
     1. Include connectors and terminals, labeling systems, audio spade lugs, barrier strips, punch blocks or wire wrap terminals, heat shrink tubing, cable ties, solder, hangers, clamps, bolts, conduit, cable duct, cable tray, etc., required to accomplish a neat and secure installation.
     2. Terminate conductors in a spade lug and barrier strip, wire wrap terminal or punch block, so there are no unfinished or unlabeled wire connections.
     3. Minimum required installation sub-kits:
        1. System Grounding:
           1. Provide required cable and installation hardware for effective ground path, including the following:

Control Cable Shields.

Data Cable Shields.

Equipment Racks.

Equipment Cabinets.

Conduits.

Ducts.

Cable Trays.

Power Panels.

Connector Panels.

Grounding Blocks.

* + - * 1. Bond radio equipment to earth ground via internal building wiring, according to NEC.
      1. Wire and Cable: Provide connectors and terminals, punch blocks, tie wraps, hangers, clamps, labels, etc. required to accomplish termination in an orderly installation.
      2. Conduit, Cable Duct, and Cable Tray: Provide conduit, duct, trays, junction boxes, back boxes, cover plates, feed through nipples, hangers, clamps, other hardware required to accomplish a neat and secure conduit, cable duct, cable tray installation in accordance with NEC and documents.
      3. Equipment Interface: Provide any items or quantity of equipment, cable, mounting hardware and materials to interface systems with identified sub-systems, according to OEM requirements and construction documents.
      4. Labels: Provide any item or quantity of labels, tools, stencils, and materials to label each subsystem according to OEM requirements, as-installed drawings, and construction documents.
    1. Cross-Connection System (CCS) Equipment Breakout, Termination Connector (or Bulkhead), and Patch Panels:
       1. Connector Panels: Flat smooth 3.175 mm (1/8 inch) thick solid aluminum, custom designed, fitted and installed in cabinet. Install bulkhead equipment connectors on panel to enable cabinet equipment’s signal, control, and coaxial cables to be connected through panel. Match panel color to cabinet installed.
          1. Voice (or Telephone):

Provide industry standard Type 110 (minimum) punch blocks for voice or telephone, and control wiring instead of patch panels, each being certified for category 5e, //6//.

IDC punch blocks (with internal RJ45 jacks) are acceptable for use in CCS when designed for Category 5e, // 6// and the size and type of cable used.

Secure punch block strips to OEM designed physical anchoring unit on a wall location in TRS; console, cabinet, rail, panel, etc. mounting is permitted at OEM recommendation and as accepted by COR. Punch blocks are not permitted for Class II or 120 VAC power wiring.

Technical Characteristics:

Number of Horizontal Rows: Minimum 100.

Number of Terminals per Row: Minimum 4.

Terminal Protector: Required for each used or unused terminal.

Insulation Splicing: Required between each row of terminals.

* + - * 1. Digital or High Speed Data:

Provide 480 mm (19 inches) horizontal EIA/ECA 310 rack mountable patch panel with EIA/ECA 310 standard spaced vertical mounting holes for digital or high-speed data service CSS, with modular female Category 5E (or on a case by case basis Category 6// 6A// for specialized powered systems accepted by SMCS 005OP2H3, (202) 461-5310, OI&T and FMS Services, and COR) RJ45 jacks designed for size and type of UTP or F/UTP cable installed in rows.

Technical Characteristics:

Number of Horizontal Rows: Minimum 2.

Number of Jacks Per Row: Minimum 24.

Type of Jacks: RJ45.

Terminal Protector: Required for each used or unused jack.

Insulation: Required between each row of jacks.

SPEC WRITER NOTE:

1. Include following subsection as appropriate for existing facilities only.

* 1. EXISTING WIRING
     1. Reuse existing wiring only where indicated on plans and accepted by SMCS 005OP2H3.
     2. Only existing wiring that conforms to specifications and applicable codes can be reused; existing wiring that does not meet these requirements cannot be reused and must be removed by contractor.

1. EXECUTION
   1. installation
      1. General:
         1. Install wiring in cable tray or raceway.
         2. Seal cable entering a building from underground, between wire and conduit where cable exits conduit, with non-hardening approved compound.
         3. Wire Pulling:
            1. Provide installation equipment that prevents cutting or abrasion of insulation during pulling of cables.
            2. Use ropes made of nonmetallic material for pulling feeders.
            3. Attach pulling lines for feeders by means of either woven basket grips or pulling eyes attached to conductors, as accepted by COR.
            4. Pull multiple cables into a single conduit together.
      2. Installation in Maintenance or Man holes:
         1. Install and support cables in maintenance holes on steel racks with porcelain or equal insulators.
         2. Train cables around maintenance hole walls, but do not bend to a radius less than six times overall cable diameter.
         3. //Fireproofing:
            1. Install fireproofing where low voltage cables are installed in same maintenance holes with high voltage cables; also cover low voltage cables with arc proof and fireproof tape.
            2. Use tape of same type used for high voltage cables, and apply tape in a single layer, one-half lapped or as recommended by manufacturer. Install tape with coated side towards the cable and extend minimum 25 mm (1 inch) into each duct.
            3. Secure tape in place by a random wrap of glass cloth tape. //
      3. Control, Communication and Signal Wiring Installation:
         1. Unless otherwise specified in other sections, provide wiring and connect to equipment/devices to perform required functions as indicated.
         2. Install separate cables for each system so that malfunctions in any system does not affect other systems, except where otherwise required.
         3. Group wires and cables according to service (i.e. AC, grounds, signal, DC, control, etc.); DC, control and signal cables can be included with any group.
         4. Form wires and cables to not change position in group throughout the conduit run. Bundle wires and cables in accepted signal duct, conduit, cable ducts, or cable trays neatly formed, tied off in 600 mm to 900 mm (24 inch to 36 inch) lengths to not change position in group throughout run.
         5. Concealed splices are not allowed.
         6. Separate, organize, bundle, and route wires or cables to restrict EMI, channel crosstalk, or feedback oscillation inside any enclosure.
         7. Looking at any enclosure from the rear (wall mounted enclosures, junction, pull or interface boxes from the front), locate AC power, DC and speaker wires or cables on the left; coaxial, control, microphone and line level audio and data wires or cables, on the right.
         8. Provide ties and fasteners that do not damage or distort wires or cables. Limit spacing between tied points to maximum 150 mm (6 inches).
         9. Install wires or cables outside of buildings in conduit, secured to solid building structures.
         10. Wires or cables must be specifically accepted, on a case by case basis, to be installed outside of conduit. Bundled wires or cables must be tied at minimum 460 mm (18 inches) intervals to a solid building structure; bundled wires or cables must have ultra violet protection and be waterproof (including all connections).
         11. Laying wires or cables directly on roof tops, ladders, drooping down walls, walkways, floors, etc. is not permitted.
         12. Wires or cables installed outside of conduit, cable trays, wireways, cable duct, etc.:
             1. Only when authorized, can wires or cables be identified and approved to be installed outside of conduit.
             2. Provide wire or cable rated plenum and OEM certified for use in air plenums.
             3. Provide wires and cables hidden, protected, fastened and tied at maximum 600 mm (24 inches) intervals, to building structure.
             4. Provide closer wire or cable fastening intervals to prevent sagging, maintain clearance above suspended ceilings.
             5. Remove unsightly wiring and cabling from view, and discourage tampering and vandalism.
             6. Sleeve and seal wire or cable runs, not installed in conduit, that penetrate outside building walls, supporting walls, and two hour fire barriers, with an approved fire retardant sealant.
      4. AC Power:
         1. Bond to ground contractor-installed equipment and identified Government-furnished equipment, to eliminate shock hazards and to minimize ground loops, common mode returns, noise pickup, crosstalk, etc. for total ground resistance of 0.1 Ohm or less.
         2. Use of conduit, signal duct or cable trays as system or electrical ground is not permitted; use these items only for dissipation of internally generated static charges (not to be confused with externally generated lightning) that can be applied or generated outside mechanical and physical confines of system to earth ground. Discovery of improper system grounding is grounds to declare system unacceptable and termination of all system acceptance testing.
         3. Cabinet Bus: Extend a common ground bus of at least #10 AWG solid copper wire throughout each equipment cabinet and bond to system ground. Provide a separate isolated ground connection from each equipment cabinet ground bus to system ground. Do not tie equipment ground busses together.
         4. Equipment: Bond equipment to cabinet bus with copper braid equivalent to at least #12 AWG. Self-grounding equipment enclosures, racks or cabinets, that provide OEM certified functional ground connections through physical contact with installed equipment, are acceptable alternatives.
   2. equipment IDENTIFICATION
      1. Control, Communication and Signal System Identification:
         1. Install a permanent wire marker on each wire at each termination.
         2. Identify cables with numbers and letters on the labels corresponding to those on wiring diagrams used for installing systems.
         3. Install labels retaining their markings after cleaning.
         4. In each maintenance hole (manhole) and handhole, install embossed brass tags to identify system served and function.
      2. Labeling:
         1. Industry Standard: ANSI/TIA-606-B.
         2. Print lettering for voice and data circuits using // laser printers // thermal ink transfer process //\_\_\_\_\_\_ //; handwritten labels are not acceptable.
         3. Cable and Wires (hereinafter referred to as “cable”): Label cables at both ends in accordance with industry standard. Provide permanent labels in contrasting colors. Identify cables matching system Record Wiring Diagrams.
         4. Equipment: Permanently labeled system equipment with contrasting plastic laminate or bakelite material. Label system equipment on face of unit corresponding to its source.
         5. Conduit, Cable Duct, and Cable Tray: Label conduit, duct and tray, including utilized GFE, with permanent marking devices or spray painted stenciling a minimum of 3 meters (10 ft.) identifying system. Label each enclosure according to this standard.
         6. Termination Hardware: Label workstation outlets and patch panel connections using color coded labels with identifiers in accordance with industry standard and Record Wiring Diagrams.
   3. TESTING
      1. Minimum test requirements are for impedance compliance, inductance, capacitance, signal level compliance, opens, shorts, cross talk, noise, and distortion, and split pairs on cables in frequency ranges specified.
      2. Tests required for data cable must be made to confirm operation of this cable at minimum 10 Mega (M) Hertz (Hz) full bandwidth, fully channel loaded and a Bit Error Rate of a minimum of 10-6 at maximum rate of speed.
      3. Provide cable installation and test records at acceptance testing to COR and thereafter maintain in facility’s telephone switch room.
      4. Record changes (used pair, failed pair, etc.) in these records as change occurs.
      5. Test cables after installation and replace any defective cables.

- - - E N D - - -