SECTION 27 16 19
COMMUNICATIONS PATCH CORDS, STATION CORDS, AND CROSS CONNECT WIRE

SPEC WRITER NOTES:

1. Delete between // // if not applicable to project. Also delete any other item or paragraph not applicable in the section and renumber the paragraphs.

PART 1 - GENERAL

1.1 DESCRIPTION:

This section specifies requirements for telecommunications patch cords.

**1.2 SUMMARY**

 Section Includes:

1. Copper (UTP) Patch Cables.
2. Fiber Optic Patch Cables.

**1.3 REFERENCES**

 A. VA Infrastructure Standard for Telecommunications Spaces.

1.4 RELATED WORK:

 A. Termination equipment: Section 27 11 19, COMMUNICATIONS TERMINATION BLOCKS AND PATCH PANELS.

B. Cable labeling requirements: Section 27 05 53, IDENTIFICATION FOR COMMUNICATIONS SYSTEMS.

* 1. SUBMITTALS:

A. Submit in accordance with Section 27 05 00, COMMON WORK RESULTS FOR COMMUNICATIONS SYSTEMS.

PART 2 - PRODUCTS

**2.1 COPPER (UTP) PATCH CABLES.**

A. Performance Category. Patch cables shall meet the Category 6A performance requirements. Category 6A connectors are required.

B. Termination Method. Factory pre-terminated TIA 568B.

C. Conductor Size. 22-28AWG. Where 28AWG patch cords are specified, the overall horizontal channel distance is reduced.

D. Length. Patch cords of the shortest appropriate length shall be used.

**2.2 FIBER OPTIC PATCH CABLES.**

A. Construction. Fiber patch cords shall be constructed of pairs (2-strands) of // multimode laser-enhanced 50/125μm // //single mode laser-optimized 9/125μm // fiber.

B. Performance Category. Multimode patch cords shall meet the // OM4 // // OM5 // performance requirements.

C. Connectors. Duplex Lucent connector (LC) connectors are required. Where polarity requirements are not known, reversible polarity duplex LC connectors are specified on one end.

D. Termination Method. Factory pre-terminated.

E. Length. Patch cords of the shortest appropriate length shall be used.

PART 3 - EXECUTION

**3.1** **IMPLEMENTATION.**

A. Patch cords shall not be used to connect equipment in different server cabinets.

B. Patch cords shall be neatly installed using cable management equipment and following cable management principles.

C. Upon installation patch cords shall be labeled in accordance with the requirements of the VA Infrastructure Standard for Telecommunications Spaces.

‑ ‑ ‑ E N D ‑ ‑ ‑