# Appendix C - Sample Commissioning Agent Request for Proposals

Editor’s Note:  The following is a sample Request for Proposals (RFP) for an Indefinite Delivery, Indefinite Quantity commissioning services contract.  This sample document assumes the VA will solicit qualifications and award one or more commissioning agent contracts by the various VA Regional CFM Offices, VA VISNs, or by VA Medical Centers via IDIQ contracts with ordering officer authority given to the various Contracting Officers.  The RFP should be modified and adapted as necessary to meet the specific needs of the Region or VISN.  It can also be adapted by VACO to request proposals for specific very large projects where Central Office oversight is desired.

The sample document requests qualifications from qualified commissioning firms.  Award of an IDIQ contract will be qualifications-based without pricing for specific projects.  Subsequent task orders will request firm fixed pricing via competition between the IDIQ firms. -

When the proposals have been evaluated, a short list of prospective firms can be established.  These firms can be interviewed so the VA and the VISN can evaluate the firm and the key personnel face-to-face.

When evaluations have been completed, the VA or the VISN will award IDIQ contracts to three or more best qualified commissioning firms.  As required for specific projects, the VA or VISN will compete commissioning services between the firms to provide commissioning services for the project.

The sample RFP that follows is too big for a synopsis; a synopsis should be prepared in accordance with contracting requirements that can be used in the announcement of the RFP.  Using the template that follows would be a good basis for a solicitation.  The sample will need to be tailored to the specific solicitation.  The acquisition of a Commissioning Agent may require development of an acquisition plan, source selection plan, etc. on the contracting side, and the sample RFP should be used for informational purposes only.

Request for Proposals

Commissioning Agent Services

//Project Title//

# GENERAL INFORMATION:

## Overview:

Editor’s Note:  In the paragraph below, identify the issuing office.  If this is an IDIQ RFP, retain the language shown, edit as necessary.  It this is an RFP for a specific project, delete the language in braces and insert language for the specific project.  Add information in brackets as necessary for the specific RFP.

A.	The U.S. Department of Veterans Affairs, //insert issuing office// hereby solicits for Qualifications to provide Whole Building Commissioning Services //on an Indefinite Delivery/Indefinite Quantity (ID/IQ) Contract basis / for the subject project// to be procured in accordance with the Federal Acquisition Regulation Part 36. It is anticipated that //these ID/IQ contracts / this contract// will be negotiated and awarded in //insert timeframe//. The initial contract periods will consist of one base year with four (4) option years per contract. The amount of work will not exceed $ //insert amount// per year. Work will be issued by negotiated firm-fixed-price //task orders not to exceed the maximum limit per task order / contract//.

## Pre-Proposal Conference:

A.	A //voluntary / mandatory// Pre-Proposal Conference will be held on //insert date and time// at //insert location//.  The purpose of this conference will be to review the RFP and to provide an opportunity to ask any questions or receive further information.

## Proposal Schedule and Submission Deadline:

A.	The schedule for this solicitation is as follows:

1.	Request for Proposals release:  //insert date//

2.	Pre-Proposal Conference: //insert date & time//

3.	Questions / Requests for Clarification due:  //insert date & time//

4.	Responses to Questions & Clarifications release:  //insert date//

5.	Proposals Due: //insert date & time//

## Questions of Requests for Clarification

A.	All questions, requests for clarification or other correspondence relative to this Request for Proposals shall be addressed to:

1.	//insert name of point of contact//

2.	//address//

3.	//City, State Zip//

4.	Phone: //xxx-xxx-xxxx//

5.	Fax: //xxx-xxx-xxxx//

6.	Email: //insert email address//

B.	Copies shall be sent to:

1.	//insert name of Contracting Officer//

2.	//address//

3.	//City, State Zip//

4.	Phone: //xxx-xxx-xxxx//

5.	Fax: //xxx-xxx-xxxx//

6.	Email: //insert email address//

C.	Questions or requests for clarification shall be submitted in writing only.  Any verbal responses to questions or clarifications are not official and are not binding on this RFP unless confirmed in writing.  Questions or requests for clarifications, along with the responses will be distributed in writing to all parties registered to receive this RFP

# Project Overview

## Project Description:

A.	//For an IDIQ RFP – insert a general description of the types of projects that may be included in task orders//.

B.	//For a specific project RFP – insert a general description of the project//.

## Project Location:

A.	//For an IDIQ RFP – insert a description of the locations where projects may be located for individual task orders//.

B.	//For a specific project RFP – insert the project location//.

## Project Team

A.	//For an IDIQ RFP – insert a general list of typical project team members, including VA Project Manager, VA Resident Engineer, A/E, Peer Reviewer, and Prime Contractor//.

B.	//For a specific project – insert a list of project team members with name/firm, if available, for the VA Project Manager, VA Resident Engineer, A/E, Peer Reviewer, Prime Contractor//.

## Project Schedule

A.	//For an IDIQ RFP – insert a typical schedule for a project and indicate that the schedule is generic and is subject to change.  The intent of providing the schedule is to give the proposing firm an idea of how long a typical project will require for design, construction, and warranty phases//.

B.	//For a specific project – insert the proposed project schedule and indicate the schedule is subject to change.  The intent is to provide the proposing firm an idea of how long the project will require for design, construction and warranty phases.  All proposals should be based on the initial project schedule provided in the RFP//.

## Estimated Project Construction Cost

A.	//For an IDIQ RFP – provide a range of probable project construction costs for the types of projects that may be assigned to a specific task order//.

B.	//For a specific project RFP – provide a budget construction cost to give the proposing firm an idea of the anticipated construction costs//.

# Commissioning Agent Qualifications

## Firm and Individual Experience

A.	The firm and the designated Commissioning Authority shall have a minimum of //five (5) years’ / insert number of years// experience in providing Total Building Commissioning Services and shall be regularly employed as a Commissioning Provider.

B.	The Commissioning Authority is an objective, independent advocate for the Contracting Officer. The Commissioning Authority shall have current engineering knowledge and extensive hands-on field experience regarding building systems; the physical principles of building systems performance; building systems start-ups, balancing, functional testing, and troubleshooting; operation and maintenance procedures; and the building design and construction process.

C.	The Commissioning firm and the designated Commissioning Authority shall have successful commissioning experience for projects that are similar to the project. The Firm and designated Commissioning Authority shall have been the principal commissioning authority on a least //three (3) / insert number// comparable projects that have been completed within the previous five (5) years.

D.	The Commissioning Authority shall have experience in the quality process.

E.	The Commissioning Authority shall be knowledgeable in building operation and maintenance, including training of operations and maintenance personnel.

F.	The Commissioning Authority shall have excellent verbal and written communications skills, be highly organized, and able to work with all levels of management, technical, and trades personnel.

G.	 personnel and the capability to sustain loss of assigned personnel without compromising quality and timeliness of performance.

H.	The Commissioning Authority shall be an independent contractor and not an employee of the Architect/Engineer, Design-Build Contractor, Prime Contractor or General Contractor on //the projects / this project//.

## Firm and Individual Certifications

A.	The proposed commissioning firm should be certified by at least one of the following agencies:

1.	National Environmental Balancing Bureau (NEBB)

2.	AABC Commissioning Group (AGC)

3.	Building Commissioning Association (BCxA)

b.	The proposed Commissioning Agent should be certified by one of the following organizations to supervise execution of the commissioning process:

1.	National Environmental Balancing Bureau (NEBB)

2.	AABC Commissioning Group (AGC)

3.	Building Commissioning Association (BCxA)

Editor’s Note:  Retain the following paragraph if the scope of commissioning services includes commissioning fire suppression systems or smoke control systems.

B.	//The Fire Protection Commissioning Specialist should be a registered Fire Protection Engineer in at least one state.  He/she should have a minimum of 5 years’ experience with design, installation, inspection, or testing of fire protection systems, and/or smoke control systems.//

Editor’s Note:  Retain the following paragraph if the scope of commissioning services includes commissioning the building envelope.

C.	//The Building Envelope Commissioning Specialist should be a Registered Architect in at least one state.  He/she should also have a minimum of five (5) years’ experience with design, installation, or inspection of building envelope components.//

D.	The Controls Commissioning Specialist should have a minimum of 5 years’ experience in design, installation, programming, inspection, or testing of direct digital control systems for HVAC systems.

Editor’s Note:  Edit the following paragraph to include engineering degrees and experience appropriate for the projects.

E.	Key members of the Commissioning Authority’s commissioning team should have a bachelor’s degree in //Mechanical//, //Electrical//, //Architectural// engineering. A Professional Engineer license in at least one jurisdiction is desired. Over 5 years field experience in //building systems operations, maintenance, and troubleshooting//, //HVAC system installation, maintenance, and troubleshooting//, //HVAC Direct Digital Control system installation, programming, maintenance, and troubleshooting//, //electrical system installation, maintenance, and troubleshooting//, //other applicable trade contracting// experience may be deemed equivalent experience for the bachelor’s degree.

## SBA Program

Editor’s Note:  Include any requirements or goals for small, veteran, minority, or woman owned business participation.

A.	//Insert any requirements or goals for small business, veteran-owned, minority-owned, woman-owned business enterprise requirements.//

B.	The VA is committed to the utilization of Veteran-owned, Disabled Veteran-Owned, Woman Owned, Small Disadvantaged Businesses, or other small business firms   Identify whether your firm, or any sub-consultant, is qualified/certified as one of these enterprises.

# Commissioning Services

## Scope of Commissioning Services

A.	Building Commissioning is a systematic approach to improving system performance, operation & maintenance, indoor air quality & thermal comfort, and energy efficiency, as well as benefits like improving occupant comfort, health & welfare, and productivity, in both new and existing buildings. These activities are not, as many owners and managers believe, part of the typical design and construction process or part of standard operation & maintenance service contracts. Commissioning goes beyond testing, adjusting and balancing (TAB) and traditional inspections. Commissioning involves functional testing to determine how well the building systems, like Heating, Ventilating and Air Conditioning (HVAC) and Lighting, work together. Commissioning also seeks to determine whether the installed building equipment (e.g. chillers, boilers, motors, airflow system) meets a facility's goals or whether it needs to be adjusted to improve the efficiency and overall performance, consistent with the original design intent. The long-term life-cycle benefits of commissioning far outweigh the short-term up-front investments, as borne out by many documented case studies, both in the public and private sector building/facility infrastructure. Green building rating systems and certification programs have given a significant boost to the role of Building Commissioning, as part of the Efficient and High Performance Building stock.

B.	Whole Building Commissioning services for third-party commissioning are required for various VA facilities and infrastructure projects within the area of responsibility which //includes insert area description//. The successful Commissioning Agent will provide support to the Commissioning Process through the design, construction, acceptance, and post-acceptance phases of renovation, additions, or other projects with an estimated construction cost of //$5,000,000 to $50,000,000// per project. These contracts may support medical-related facilities (to include, but not be limited to VA Hospitals, VA medical clinics, VA dental clinics, VA Community Living Centers, and VA laboratories) as well as a broad range of other types of VA facilities (to include, but not be limited to administration, training, education, maintenance, recreation, domiciliary, central energy plants, other supporting facilities). Projects for which commissioning services would be required may include new facility construction, additions to existing facilities, and/or renovation, alteration, maintenance, repair, or upgrades to existing facilities.

C.	Commissioning Services will be provided in accordance with the Department of Veterans Affairs Commissioning Process Manual. Prospective proposers shall review the Whole Building Commissioning Process Manual available on the VA Technical Information Library at http://www.cfm.va.gov/til/.

D.	The following tables describe the commissioning services and deliverables to be provided by the Commissioning Agent:

Editor’s Note:  Edit the following tables as necessary to adjust the scope of services to the specific project.  The tables provided in Appendix B to the Whole Building Commissioning Process Manual can be used to edit the table, or edits can be made directly in the table below.

| Commissioning Agent Task/Deliverables Description Pre-Design Phase |  |  |
| --- | --- | --- |
| Project Phase/ Cx Task | Commissioning Task Description | Commissioning Deliverables |
| PRE-DESIGN PHASE |  |  |
| Pre-Design Commissioning Kickoff Meeting | Conduct Pre-Design Commissioning Kickoff Meeting with the VA and the Design Team. Establish or review Owner’s Project Requirements (OPR), goals, objectives, and preliminary schedule. Establish commissioning goals and objectives. Establish the purpose and proposed process for commissioning the project. Establish the individual roles of each participating commissioning team member. Establish systems to be commissioned and preliminary acceptance criteria. | Draft Commissioning Plan Meeting Minutes Preliminary Owner’s Project Requirements |

| Commissioning Agent Task/Deliverables Description Design Phase |  |  |
| --- | --- | --- |
| Project Phase/ Cx Task | Commissioning Task Description | Commissioning Deliverables |
| SD1 PHASE |  |  |
| Design Submission Review | Complete a thorough commissioning review of the SD1 submittal documents and submitted criteria to establish the systems to be designed and installed in compliance with the Owner’s Project Requirements (OPR). Review is conducted in conjunction with the IDIQ-AE Peer Review. Documents provided to the Commissioning Agent should include, SD1 Design Narrative and other submittal documents required by PG 18-15, as well as other pertinent documents. | Design Phase Commissioning Issues Log (Incorporate Commissioning Agent review comments into Dr Checks for Project Tracking – Retain for Design Phase Cx Report) |
| Design Narrative | Review and Reconcile the Project Design Narrative. Narrative should incorporate OPR requirements from VA Standards and other Project Documents. Design Narrative should describe designer’s approach to the project requirements. Design Narrative can include both the Owner’s Project Requirements (OPR) and the Basis of Design (BOD) information. Likewise separate documents can be developed and retained in the project record. | Design Phase Commissioning Issues Log (Incorporate commissioning review comments into Dr Checks for Project Tracking – Retain for Design Phase Cx Report) |
| Commissioning Plan | Develop the Project Design Phase Commissioning Plan that outlines process requirements, deliverables, roles, responsibilities, schedule and milestones. Provide a copy of the Commissioning Plan to the A/E. The A/E will incorporate the Commissioning Plan into the Design Narrative as described in PG 18-15 | Project Design Phase Commissioning Plan |
| Duration Schedule for Commissioning Activities | Based on the Project Design Phase Commissioning Plan, prepare a duration schedule for the design phase commissioning activities required by the commissioning plan. This duration schedule should include Design Phase Activities. The Duration Schedule should provide sufficient detail to comply with the AE Team CPM scheduling requirements as outlined in PG 18-15. | Design Phase Commissioning Duration Schedule – Incorporate into Commissioning Plan |
| Design Review Meeting | Attend and participate in SD1 Design Review Meeting. Provide clarifications for identified Commissioning Issues as appropriate. Incorporate other comments or issues identified at Review Meeting that impact project commissioning into Commissioning Issues Log. | Revised Design Phase Commissioning Issue Log. (Note that resolution of some issues may be deferred to later design stages.) |
| SD2 PHASE |  |  |
| Design Submission Review | Complete a thorough commissioning review of the SD2 submittal documents and submitted criteria to establish the systems to be designed and installed in compliance with the OPR. Documents provided to the Commissioning Agent should include, SD2 Design Narrative, calculations, room locations and preliminary layouts and other submittal documents required by PGA 18-15, as well as other pertinent documents. | Design Phase Commissioning Issues Log (Incorporate commissioning review comments into Dr. Checks for Project Tracking – Retain for Design Phase Cx Report) |
| Design Narrative | Review the updated Project Design Narrative. The Design Narrative should incorporate OPR requirements from VA Standards and other Project Documents. Design Narrative should describe designer’s approach to the project requirements. | Design Phase Commissioning Issues Log (Incorporate review comments into Dr Checks for Project Tracking – Retain for Design Phase Cx Report) |
| Commissioning Plan | Update the Project Design Phase Commissioning Plan. Provide a copy of the Commissioning Plan to the A/E. The A/E will incorporate the Commissioning Plan into the Design Narrative as described in PG 18-15 | Updated Project Design Phase Commissioning Plan |
| Duration Schedule for Commissioning Activities | Based on the Project Design Phase Commissioning Plan, prepare a duration schedule for the Design Phase commissioning activities required by the commissioning plan. This duration schedule should include Design Phase Activities. The Duration Schedule should provide sufficient detail to comply with the AE Team CPM scheduling requirements as outlined in PG 18-15. | Design Phase Commissioning Duration Schedule – Incorporate into Commissioning Plan |
| Commissioning Specifications | Provide Outline Commissioning Specifications Sections utilizing the VA Master Construction Specification. Specifications shall be submitted in accordance with the requirements of PG 18-15. | Outline Commissioning Specifications Specification Coordination Matrix for Commissioning Agent/A/E coordination. |
| Design Review Meeting | Attend and participate in SD2 Design Review Meeting. Provide clarifications for identified Commissioning Issues as appropriate. Incorporate other comments or issues identified at Review Meeting that impact project commissioning into Commissioning Issues Log. | Revised Design Phase Commissioning Issue Log Note that resolution of some issues may be deferred to later design stages. |
| Design Phase Issue Log Resolution | Update the Commissioning Issues Log by recording resolutions to identified Commissioning Issues. | Revised Design Phase Commissioning Issue Log |
| DD1 PHASE |  |  |
| Design Submission Review | Complete a thorough commissioning review of the DD1 submittal documents and submitted criteria to establish the systems to be designed and installed in compliance with the OPR. Documents provided to the Commissioning Agent should include: DD1 Updated Design Narrative, calculations, equipment schedules, system and control schematic diagrams and appropriate schematics and other submittal documents required by PG 18-15, as well as other pertinent documents. | Design Phase Commissioning Issues Log (Incorporate review comments into Dr. Checks for Project Tracking – Retain for Design Phase Cx Report) |
| Design Narrative | Review the updated Project Design Narrative. The Design Narrative should be updated to reflect the evolution of the project design and note all significant deviations from prior version for ease of review and reconciliation. Design Narrative should describe designer’s approach to the project requirements. | Design Phase Commissioning Issues Log (Incorporate review comments into Dr. Checks for Project Tracking – Retain for Design Phase Cx Report) |
| Design Phase Controls Meeting | Meet with the Design Team and VAMC to develop HVAC and other system control strategies, sequences of operation, trending, and alarms. The Commissioning Agent acts as a advocate for the VAMC and the facilities operations staff to assist the Design Team in developing realistic operating strategies and sequences of operations that will enable the facilities operations staff to operate the building systems to sustain the operational, energy and other systems parameters throughout the project life cycle. | Meeting Notes |
| Commissioning Plan | Update the Project Design Phase Commissioning Plan, including any revisions to Commissioning Team Members, Schedules and other modifications required by the progress of the project. Prepare a Draft Construction Phase Commissioning Plan, including systems to be commissioned, an outline of construction phase roles and responsibilities, and an outline of required system documentation requirements. Provide a copy of the updated Design Phase Commissioning Plan to the A/E. The A/E will incorporate the Commissioning Plan into the Design Narrative as described in PG 18-15 | Updated Project Design Phase Commissioning Plan Draft Construction Phase Commissioning Plan |
| Duration Schedule for Commissioning Activities | Based on the Project Design Phase Commissioning Plan, prepare a duration schedule for the commissioning activities required by the commissioning plan. This duration schedule should include Design Phase Activities. The Duration Schedule should provide sufficient detail to comply with the AE Team CPM scheduling requirements as outlined in PG 18-15. Based on the Draft Construction Phase Commissioning Plan, prepare a preliminary duration schedule for Construction Phase Commissioning Activities. Incorporate the draft duration schedule into the Draft Construction Phase Commissioning Plan. | Commissioning Duration Schedule – Incorporate into Commissioning Plan Draft Construction Phase Commissioning Duration Schedule – Incorporate into the Draft Construction Phase Commissioning Plan. |
| Commissioning Specifications | Provide Draft Commissioning Specifications Sections utilizing the VA Master Construction Specification. Specifications shall be submitted in accordance with the requirements of PG 18-15. Provide a Specification Coordination Matrix that outlines the commissioning-related language that needs to be included in the individual equipment and technical specifications. | Draft Commissioning Specifications Specification Coordination Matrix for Commissioning Agent/A/E coordination. |
| Design Review Meeting | Attend and participate in DD1 Design Review Meeting. Provide clarifications for identified Commissioning Issues as appropriate. Incorporate other comments or issues identified at Review Meeting that impact project commissioning into Commissioning Issues Log. | Revised Design Phase Commissioning Issue Log. (Incorporate review comments into Dr. Checks for Project Tracking – Retain for Design Phase Cx Report) (Note that resolution of some issues may be deferred to later design stages.) |
| Design Phase Issue Log Resolution | Update the Commissioning Issues Log by recording resolutions to identified Commissioning Issues. | Revised Design Phase Commissioning Issue Log (Incorporate review comments into Dr. Checks for Project Tracking – Retain for Design Phase Cx Report) |
| DD2 PHASE |  |  |
| Design Submission Review | Complete a thorough review of the DD2 submittal documents and submitted criteria to establish the systems to be designed and installed in compliance with the OPR. Documents provided to the Commissioning Agent should include: DD2 Updated Design Narrative, calculations, equipment schedules, system and control schematic diagrams, floor plans and appropriate schematics and other submittal documents required by PG 18-15, as well as other pertinent documents. | Design Phase Commissioning Issues Log (Incorporate review comments into Dr. Checks for Project Tracking – Retain for Design Phase Cx Report) |
| Design Narrative | Commissioning Agent to update, review and reconcile the Project Design Narrative. The Design Narrative should reflect the evolution of the project design and note all significant deviations from prior version for ease of review and reconciliation. Design Narrative should describe designer’s response to the project requirements. Submit the updated Design Narrative to the AE team for review and comment. Incorporate review comments into the updated Design Narrative as necessary. | Design Phase Commissioning Issues Log |
| Commissioning Plan | Update the Project Design Phase Commissioning Plan, including any revisions to Commissioning Team Members, Schedules and other modifications required by the progress of the project. Update the Construction Phase Commissioning Plan, including systems to be commissioned, an outline of construction phase roles and responsibilities, and an outline of required system documentation requirements. Include the updated Commissioning Plan in the revised Design Narrative | Updated Project Commissioning Plan |
| Commissioning Specifications | Provide Preliminary Commissioning Specifications Sections utilizing the VA Master Construction Specification. Specifications shall be submitted in accordance with the requirements of PG 18-15. Review individual equipment and technical sections to ensure commissioning-related language has been included as provided in the Commissioning Specification Coordination Matrix. | Preliminary Commissioning Specifications Marked up equipment and technical specification sections showing any revisions to commissioning-related language. Specification Coordination Matrix for Commissioning Agent/A/E coordination. |
| Duration Schedule for Commissioning Activities | Based on the Project Design Phase Commissioning Plan, prepare an updated duration schedule for the design phase commissioning activities required by the commissioning plan. This duration schedule should include Design Phase Activities. The Duration Schedule should provide sufficient detail to comply with the AE Team CPM scheduling requirements as outlined in PG 18-15. Based on the Project Construction Phase Commissioning Plan and the DD2 Phase design submission, update the draft Construction Phase Commissioning Duration Schedule. Incorporate the revised Construction Phase Duration Schedule into the Draft Commissioning Phase Commissioning Plan. | Design Phase Commissioning Duration Schedule – Incorporate into Design Phase Commissioning Plan Construction Phase Commissioning Duration Schedule – Incorporate into Construction Phase Commissioning Plan |
| Develop Preliminary Pre-Functional Checklists (PFC’s) | The Commissioning Agent will prepare Preliminary Pre Functional Checklists (PFC) for type of system to be commissioned and distribute to all Cx Team members for review and comment. A completed PFC indicates the system and its related equipment is ready for Systems Functional Performance Testing. Preliminary Pre-Functional Checklists shall be included in the Construction Phase Commissioning Plan and the Commissioning Specifications. | Preliminary Pre Functional Checklists (PFC’s) |
| Develop Preliminary Systems Functional Performance Test (FPT’s) Procedures | Based on the systems to be commissioned and the systems shown in the DD2 submittal, the Commissioning Agent will prepare Preliminary Systems Functional Performance Test Procedures (FPT’s). Preliminary FPTs shall be included in the Construction Phase Commissioning Plan and the Commissioning Specifications. | Preliminary Systems Functional Performance Test Procedures (FPT’s) |
| Design Phase Controls Meeting | Meet with the Design Team and VAMC to update HVAC and other system control strategies, sequences of operation, trending, and alarms. The Commissioning Agent acts as an advocate for the VAMC and the facilities operations staff to assist the Design Team in developing realistic operating strategies and sequences of operations that will enable the facilities operations staff to operate the building systems to sustain the operational, energy and other systems parameters throughout the project life cycle. | Meeting Notes |
| Design Review Meeting | Attend and participate in DD2 Design Review Meeting. Provide clarifications for identified Commissioning Issues as appropriate. Incorporate other comments or issues identified at Review Meeting that impact project commissioning into Commissioning Issues Log. | Revised Design Phase Commissioning Issue Log. (Incorporate review comments into Dr. Checks for Project Tracking – Retain for Design Phase Cx Report) (Note that resolution of some issues may be deferred to later design stages.) |
| Design Phase Issue Log Resolution | Update the Commissioning Issues Log by recording resolutions to identified Commissioning Issues. | Revised Design Phase Commissioning Issue Log (Incorporate review comments into Dr. Checks for Project Tracking – Retain for Design Phase Cx Report) |
| CD1 PHASE |  |  |
| Design Submission Review | Complete a thorough commissioning review of the CD1 submittal documents and submitted criteria to establish the systems to be designed and installed in compliance with the OPR. Documents provided to the Commissioning Agent should include: calculations, equipment schedules, system and control schematic diagrams, floor plans and appropriate schematics and other submittal documents required by PG 18-15, as well as other pertinent documents. | Design Phase Commissioning Issues Log (Incorporate review comments into Dr. Checks for Project Tracking – Retain for Design Phase Cx Report) |
| Design Narrative | Commissioning Agent to update, review and reconcile the Project Design Narrative. The Design Narrative should be updated to reflect the evolution of the project design and note all significant deviations from prior version for ease of review and reconciliation. Design Narrative should describe designer’s response to the project requirements. Submit the updated Design Narrative to the AE team for review and comment. Incorporate review comments into the updated Design Narrative as necessary. | Revised Design Narrative |
| Commissioning Plan | Update the Project Design Phase Commissioning Plan, including any revisions to Commissioning Team Members, Schedules and other modifications required by the progress of the project. Update the Construction Phase Commissioning Plan, including systems to be commissioned, an outline of construction phase roles and responsibilities, and an outline of required system documentation requirements. Include the updated Commissioning Plan in the revised Design Narrative | Updated Design Phase Project Commissioning Plan Updated Construction Phase Project Commissioning Plan |
| Duration Schedule for Commissioning Activities | Based on the Project Design Phase Commissioning Plan, prepare a duration schedule for the commissioning activities required by the commissioning plan. This duration schedule should include Design Phase Activities. The Duration Schedule should provide sufficient detail to comply with the AE Team CPM scheduling requirements as outlined in PG 18-15. Based on the Project Construction Phase Commissioning Plan and the DD2 Phase design submission, update the draft Construction Phase Commissioning Duration Schedule. Incorporate the revised Construction Phase Duration Schedule into the Draft Commissioning Phase Commissioning Plan. | Design Phase Commissioning Duration Schedule – Incorporate into Design Phase Commissioning Plan Update Construction Phase Duration Schedule – Incorporate into Construction Phase Commissioning Plan |
| Commissioning Specifications | Provide Final Commissioning Specifications Sections utilizing the VA Master Construction Specification. Specifications shall be submitted in accordance with the requirements of PG 18-15. Review individual equipment and technical sections to ensure commissioning-related language has been included as provided in the Commissioning Specification Coordination Matrix. | Final Project Commissioning Specifications Marked up equipment and technical specification sections to identify any changes to commissioning-related language. |
| Develop Draft Pre-Functional Checklists (PFC’s) | The Commissioning Agent will update the Preliminary Pre Functional Checklists (PFC) to Draft Pre-Functional Checklists for eacy type of system to be commissioned and distribute to all Cx Team members for review and comment. Draft Pre-Functional Checklists shall be included in the Construction Phase Commissioning Plan and the Commissioning Specifications. | Draft Pre Functional Checklists (PFC’s) |
| Develop Preliminary Systems Functional Performance Test (FPT’s) Procedures | Based on the systems to be commissioned and the systems shown in the CD1 submittal, the Commissioning Agent will update the Preliminary Systems Functional Performance Test Procedures (FPT’s) to become Draft Systems Functional Performance Test Procedures. . Draft FPTs shall be included in the Construction Phase Commissioning Plan and the Commissioning Specifications. | Draft Systems Functional Performance Test Procedures (FPT’s) |
| Design Phase Controls Meeting | Meet with the Design Team and VAMC to update HVAC and other system control strategies, sequences of operation, trending, and alarms. The Commissioning Agent acts as a advocate for the VAMC and the facilities operations staff to assist the Design Team in developing realistic operating strategies and sequences of operations that will enable the facilities operations staff to operate the building systems to sustain the operational, energy and other systems parameters throughout the project life cycle. | Meeting Notes |
| Design Review Meeting | Attend and participate in CD1 Design Review Meeting. Provide clarifications for identified Commissioning Issues as appropriate. Incorporate other comments or issues identified at Review Meeting that impact project commissioning into Commissioning Issues Log. | Revised Design Phase Commissioning Issue Log. (Incorporate review comments into Dr. Checks for Project Tracking – Retain for Design Phase Cx Report) (Note that resolution of some issues may be deferred to later design stages.) |
| Design Phase Issue Log Resolution | Update the Commissioning Issues Log by recording resolutions to identified Commissioning Issues. | Revised Design Phase Commissioning Issue Log |
| FINAL DESIGN DOCUMENTS |  |  |
| Design Final Design Submission Review | Review Final Design Submission for resolution of Outstanding Commissioning Issues | Design Phase Commissioning Issues Log (Incorporate review comments into Dr. Checks for Project Tracking – Retain for Design Phase Cx Report) |
| Design Narrative | Commissioning Agent to provide a Final Design Narrative to Include all modifications and/or deviations from CD1 Design Narrative. The Design Narrative should be updated to reflect the evolution of the project design and note all significant deviations from prior version for ease of review and reconciliation. Design Narrative should describe designer’s response to the project requirements. Where appropriate, provide documentation of approved deviations from design standards and reasoning for same. | Revised Design Narrative |
| Commissioning Plan | Update & Submit Project Construction Phase Commissioning Plan Include the updated Commissioning Plan in the revised Design Narrative | Project Construction Phase Commissioning Plan |
| Duration Schedule for Commissioning Activities | Based on the Project Construction Phase Commissioning Plan, prepare a duration schedule for the commissioning activities required by the commissioning plan. This duration schedule should include Construction Phase Activities. The Duration Schedule should provide sufficient detail to allow the Prime Contractor to incorporate commissioning activities into the Master Project Schedule. | Construction Phase Commissioning Duration Schedule – Incorporate into Commissioning Plan |
| Commissioning Specification | Provide updated Final Cx Specifications. Specifications shall be submitted in accordance with the requirements of PG 18-15. | Updated Project Commissioning Specifications |
| Design Phase Issue Log Resolution | Record resolutions to Cx Issues on the Design Phase Commissioning Issues Log. | Revised Design Phase Commissioning Issue Log (Incorporate review comments into Dr Checks for Project Tracking – Retain for Design Phase Cx Report) |
| Design Phase Commissioning Report | Prepare Design Phase Commissioning Report to document the Design Phase commissioning process and results | Design Phase Commissioning Report |

| Commissioning Team Task/Deliverables Description Bid and Pre Construction Phase |  |  |
| --- | --- | --- |
| Project Phase/ Cx Task | Commissioning Task Description | Commissioning Deliverables |
| Pre Bid Meeting | Attend Pre Bid Meeting; provide overall description of Commissioning Process, provide clarifications for Commissioning Issues. | Meeting Notes for PM/RE Clarifications for Addendum if required |
| Pre-Construction Meeting | Attend Pre Construction Meeting and be prepared to clarify the Commissioning Process for this project (e.g., discuss commissioning representative selection). | None |

| Commissioning Team Task/Deliverables Description Construction Phase |  |  |
| --- | --- | --- |
| Project Phase/ Cx Task | Commissioning Task Description | Commissioning Deliverables |
| Commissioning Kick Off Meeting (Construction Phase) (The kickoff meeting should occur within 60 days of Notice to Proceed.) | Conduct a “Commissioning Kickoff Meeting” with the Construction Team Establish the purpose and process for commissioning the project. Establish the individual roles of each participating commissioning team member. Review the Construction Phase Commissioning Plan and Commissioning Specifications. Review the Commissioning Documents Review the Project Schedule and discuss how commissioning activities will be incorporated into the master schedule. Review Draft PFC and FPT; identify pre-requisites for functional testing. ATTENDEES: Commissioning Agent, A/E Design Team Representatives, Contractor’s Commissioning Representative, Subcontractor’s Commissioning Representatives, VA RE. | Meeting Minutes Revised Project Commissioning Plan (Include Names/Contact Information for selected Commissioning Team Members) |
| Duration Schedule for Commissioning Activities | Based on the Construction Phase Commissioning Plan, prepare a duration schedule for the commissioning activities required by the commissioning plan. This duration schedule should be incorporated into the contractor’s project schedule to track all commissioning activities of the commissioning team. | Commissioning Duration Schedule (Schedule shall be periodically updated to reflect changes in the project schedule and/or scope.) |
| Submittal & Shop Drawing Review | Review all pertinent project shop drawings necessary to support the Commissioning Process. Review of the shop drawings is for the purpose of developing appropriate Pre Functional Checklists and Systems Functional Performance Test Procedures. Submittals & Shop drawings shall be reviewed for commissionability, maintainability and for compliance to the Construction Documents. Note any issues identified in the Shop Drawing Review that might compromise the final commissioned system on the ‘Commissioning Review Log’ and submit comment to the Design Team and the RE contemporaneously with the A/E review for resolution. Comments shall be submitted in accordance with the contractual submittal review time. Comments shall be provided to the Design Team no less than 7 days prior to the Submittal Review Due Date provided that the Cx Agent has no less than 7 days to review the submittals. ANY ISSUES IDENTIFIED IN THE SUBMITTAL REVIEW THAT MIGHT REQUIRE A CONTRACT CHANGE BUT IS NECESSARY TO MEET DESIGN INTENT SHOULD BE SPECIFICALLY REFERRED TO THE RE. | Shop Drawing Cx Review List Shop Drawing Review Comments |
| Construction Phase Commissioning Plan | Based on the work completed in the items above, the Construction Phase Commissioning Plan for the project shall be periodically reviewed with the Commissioning Team and updated to reflect changes in project equipment, sequences of operations, scope or schedule and with project personnel. | Revised Project Commissioning Plan |
| Commissioning Construction Observations | During the course of construction, the Commissioning Agent will visit the site to observe the progress of construction with respect to the systems being commissioned. The focus of the observations will to verify that systems being installed comply with the Construction Documents and can be successfully configured, operated and maintained. In addition, site observations visits will be scheduled to include - Witnessing factory testing and/or contractor equipment/system start up activities; - Verification of Completed Pre Functional Checklists - Verification that the Contractor and his subcontractors are completing and documenting Pre-Test procedures required by the specifications. - Clarification and technical support for understanding and resolving Commissioning Issues. | Site Observation Reports Updated Commissioning Issues Log |
| Commissioning Team Meetings | The Commissioning Agent will hold regular commissioning team meetings to review progress of the commissioning effort and reinforce individual responsibilities. The team will review schedule, construction sequence, and completed work (PFC, PFT and FPT’s) and outstanding issues on the Commissioning Issues Log. Commissioning Team Meetings may be held at the jobsite or by teleconference depending upon the status of construction. While it is imperative that many of the Commissioning Team Meetings be held in person, during early construction phases, some meetings may be more cost effectively conducted remotely. Scheduling and location of meetings shall occur by consultation between the Commissioning Agent and the VA-RE. The Prime Contractor’s scheduler should attend approximately every other Commissioning Team Meeting to review the master schedule and any changes that will affect commissioning activities. | Commissioning Meeting Agenda and Minutes Updated Commissioning Issues Log |
| Develop Final Pre-Functional Checklists (PFC’s) | The Commissioning Agent will prepare Pre-Final Pre Functional Checklists (PFC) for the project and distribute to all Cx Team members for review and comment. The Commissioning Agent will incorporate review comments and prepare Final PFCs. An executed PFC submitted by the Prime Contractor indicates the system and its related equipment is ready for Systems Functional Performance Testing. The requirements for Pre Functional Checklists shall be coordinated with the startup requirements specified for each commissioned system. The PFC’s shall be constructed to leverage the specified contractor and vendor start activities to avoid unnecessary duplication. | Pre Functional Checklists (PFC’s) |
| Final Systems Functional Performance Test (FPT’s) Procedures | Based on construction documents and approved submittals, the Commissioning Agent will prepare Pre-Final Systems Functional Performance Test Procedures (FPT’s) for systems to be commissioned. Completed Final FPT’s will be distributed to all appropriate members of the Commissioning Team for review and comment. Final FPT’s will be issued once comments are reviewed and incorporated into final documents as appropriate. | Pre-Final and Final Systems Functional Performance Test Procedures (FPT’s) |
| Review Operations & Maintenance Manuals | The Commissioning Agent shall review Operations and Maintenance Manuals submitted by contractors for general conformance with specifications and VA’s requirements, including: If provided with the manuals, Review Preventive Maintenance Schedules provided as part of the O&M Manuals for completeness. Verify that data is provided in a manner consistent with VA process for managing Preventive Maintenance tasks. Review of O&M Manuals will include a review of system and component warranties to confirm conformance with contract requirements and adequate documentation of warranty contact information and VA obligations. Review of O&M Manuals shall be completed in accordance with the Submittal Review schedule requirements. | Updated Commissioning Issues Log |
| Review Contractor Equipment Startup Checklists, TAB Reports and PFC’s | The Commissioning Agent will review all contractor prepared Equipment Startup Checklists, TAB Reports (including “pencil” daily test results) and PFC’s to confirm that the systems are have been subject to appropriate Quality Control and Start Up procedures prior to initiation of Functional Performance Testing. Incomplete work, inadequate preparation and deficiencies will note noted and tracked on the Commissioning Issues Log. | Commissioning Issues Log |
| TAB Verification | The Commissioning Agent shall work with the TAB Contractor to verify that all Testing and Balancing work is conducted in strict accordance with the specified Procedural Standards for Testing, Adjusting and Balancing by either NEBB or AABC. The Commissioning Agent shall execute the following tasks: - Review the TAB Agenda provided by the TAB Contractor to verify that it is complete, thorough and in compliance with the specification and Procedural Standards requirements. - On the project site, the CxA shall review the calibration certificates for the instrumentation being used by the TAB Contractor during the execution of TAB activities to confirm that the instrumentation meets the requirements of the spec and the appropriate Procedural Standard. - The CxA shall periodically visit the project site and review the TAB documentation for method, reasonable values, and compliance with the specification, Procedural Standard and TAB Agenda. - Upon completion of the TAB activities, the CxA shall visit the project site with the TAB Contractor and the RE. The TAB Contractor shall demonstrate readings selected by the CxA that demonstrate that the system performance is consistent with the submitted values on the TAB report. Readings shall include Air Handling Unit total flows, static pressure control values, select outlet flows, building, and space pressures selected by the CxA as critical system operating values. | TAB Agenda Review Comments TAB Agenda Review Meeting Minutes Field Observation Reports of TAB Inspections Summary Report of TAB Verification Readings |

| Commissioning Team Task/Deliverables Description Acceptance and Testing Phase |  |  |
| --- | --- | --- |
| Project Phase/ Cx Task | Commissioning Task Description | Commissioning Deliverables |
| Systems Functional Performance Testing | The Commissioning Agent will oversee, facilitate, and document all FPT testing. Execution of FPT’s shall be executed in accordance with the Functional Testing Procedures published by the Commissioning Agent. All systems tested in accordance with the FPT’s shall be operated by the contractors in accordance with the approved FPT. Contractors shall retain responsibility for the installed systems during and after functional testing until substantial completion or final acceptance as determined by the VA. The Commissioning Agent, in collaboration with the control contractor shall include long term trends (greater than 7 days) of integrated system performance once all systems have been commissioned. The Commissioning Agent shall provide analysis of these trends to confirm that the installed systems are stable and reliable | Executed Functional Performance Tests and support documentation. Long Term Trend Data and Analysis |
| Prepare Systems Manuals | The Commissioning Agent shall work with the design team, contractor and VA to develop Systems Manuals. Manuals will contain system design, operations and sequence information that describes the design intent, operational features and appropriate operational practices necessary to sustain the system operation in accordance with the Design Narrative and the VA’s overall objectives for the facility. Systems Manual will include sections for each major system included in the commissioning process. | Project Systems Manual |
| Training Plan Review | The Commissioning Agent shall collaborate with the Prime Contractor and installing subcontractors to develop effective contractor and manufacturer training plans and agendas for general conformance with specifications and VA’s requirements. Observe training for quality of training and for general conformance with the training plan and agenda. The CxA shall observe contractor and vendor training for critical systems. The Contractor shall provide and the CxA shall maintain all attendance records and associated agendas and presentations for all training sessions. Attendance records shall be written original sign in sheets for each training session. | Compiled Training Plan Individual Training Agendas Training Attendance Sign In Sheets |
| Systems Training | The Commissioning Agent will conduct training sessions to provide systems-level training for O&M personnel. Training will include: - Review of system design, capacity, and equipment selection - Review of system operating sequences - Review of interconnection with other systems - Review of Emergency operating procedures - Review of the Project Systems Manual and its Use - Student Evaluation forms The number, duration and scope of the Systems Training sessions shall be determined by the specific requirements of the project. The training provided by the CxA does not in any way relieve the Contractor from any specified training obligations. | Systems Training Presentations (electronic) |
| Final Commissioning Report | The Commissioning Agent shall compile a comprehensive commissioning report documenting all commissioning activities, including but not limited to the following: - Executive Summary - Commissioning Scope of Work - Test methods and results - Outstanding commissioning issues - Comprehensive Commissioning Issues Log, including resolved items and a description of their resolution, - Commissioning plan, - Field Observation Reports, Status reports and other field activity documentation, - Submittal and O&M manual reviews - Training record - Completed Pre Functional Checklists - Completed Functional Performance Test protocols and support documentation - Other support documentation developed as part of the execution of the project Construction Phase Commissioning Process | Final Commissioning Report |

| Commissioning Team Task/Deliverables Description Warranty Phase |  |  |
| --- | --- | --- |
| Project Phase/ Cx Task | Commissioning Task Description | Commissioning Deliverables |
| Deferred and/or Seasonal Testing | The Commissioning Agent shall witness and document Systems Functional Performance Testing that was deferred to allow systems to be tested in appropriate seasonal conditions. Testing will be conducted in accordance with Systems Functional Performance Test Procedures. Testing support will be required from the installing contractors, EMCS Vendor and VA. Requirement for seasonal testing will be incorporated into the project specifications. As part of the Seasonal Testing Effort, the Commissioning Agent shall review systems operations with the onsite operations team and reinforce training and best operating practices of the operations team. | Executed Functional Performance Test and Support Documents Commissioning Issues Log |
| Warranty Period Site Visits | The Commissioning Agent shall make quarterly visits to the project site to reinforce training, evaluate performance of the installed systems and provide technical support to the operating team to sustain commissioned performance of the systems. | Warranty Site Visit Reports |
| Post-Occupancy Inspection | Return to the project approximately 10 months after substantial completion to review the building operation with the facility occupants and O&M staff, and to discuss outstanding issues related to commissioning. Provide suggestions for improvements to systems operation including, - Measurement & Verification Issues, - Re-Commissioning Tasks, and - Improvements in Preventive Maintenance or Operational Strategies Assist facility staff in developing warranty issues, documents and requests for service to remedy outstanding problems. As part of the Post Occupancy Inspection, the Commissioning Agent shall analyze the energy consumption records from the project site (both utility and system generated reports) and provide the team with an analysis of actual system energy performance versus predicted performance. To the extent possible, deficiencies in performance shall be analyzed to provide an understanding of the systems, components or operating strategies that may be operating outside predicted parameters. | Post Occupancy Field Visit Report Commissioning Issues Log Warranty Issues Report Systems Energy Review Report |
| Final Commissioning Report Amendment | Amend Final Commissioning Report to document the Warranty Phase commissioning activities. | Final Report Amendment |

## Commissioned Systems

A.	//Insert a discussion of the required / desired systems to be commissioned.  Discuss any sampling strategies that may be allowed.//

Editor’s Note:  Edit the following table to include the systems to be commissioned for the specific project.

While buildings are comprised of static systems (e.g., building envelope, building structure) and dynamic systems (e.g., HVAC, emergency power, elevators), the commissioning process is intended to address the ‘integrated dynamic performance of the ‘building system.’  Therefore, when considering which building systems to commission, the primary considerations are driven by the impacts of any given system on the overall performance of the building as a whole.   So, for example, the building envelope, while a static system, will have a substantial impact on the performance of the building environmental controls, particularly if the air or vapor barriers installed are deficient.  The list of commissioned systems included below is intended to identify those major systems that can have a significant impact on the ability of the integrated building system to achieve the patient safety, comfort, reliability and energy performance goals established by the OPR in the commissioning process.

The intent of the VA Standard for Whole Building Commissioning is to subject all building systems to the commissioning process.  On a case by case basis, the VA recognizes that the nature of the project and its attendant budget may require that systems be selectively commissioned to maximize the value delivered by the process.  With this in mind, the following criteria should be applied to evaluating each installed system (listed below) for inclusion in the commissioning process.

Systems with the most significant impacts on patient safety, the environmental performance, or reliability of the installed ‘building system’ should have highest priority in the commissioning process.

Systems that have traditionally caused performance or maintenance problems on a site (or similar sites) should have a high priority in the process.

Systems that have a significant dynamic performance component but may have a moderate impact on the net environmental building system performance should have a priority in the process.

The specific list of ‘Systems to be Commissioned’ included on any given project must be driven by the nature of the project, the installed systems and the opportunity to impact the quality of the installed system during the construction of the project.

| Systems To Be Commissioned |  |
| --- | --- |
| System | Description |
| Building Exterior Closure |  |
| Foundations (excluding structural) | Standard, special, slab-on-grade, vapor barriers, air barriers |
| Basements | Basement walls, crawl spaces, waterproofing, drainage |
| Superstructure | Floor construction, roof construction, sunshades, connections to adjacent structures |
| Exterior Closure | Exterior walls, exterior windows, exterior doors, louvers, grilles and sunscreens, |
| Roofing | Roof system (including parapet), roof openings (skylights, pipe chases, ducts, equipment curbs, etc.) |
| Note: | The emphasis on commissioning the above building envelope systems is on control of air flow, heat flow, noise, infrared, ultraviolet, rain penetration, moisture, durability, security, reliability, constructability, maintainability, and sustainability. |
| Specialties |  |
| Patient Bed Service Walls | Medical gas certification and cross check, electrical connections |
| Equipment |  |
| Parking Control Equipment | Barriers |
| Laboratory Fume Hoods | Fume Hood Certification |
| Biological Safety Cabinets | Cabinet Certification |
| Packaged Incinerators | Combustion Testing, Cycle Certification |
| Conveying Equipment |  |
| Electric Dumbwaiters | Interface with other systems (Fire Alarm, etc) (ASTM testing and certification by others) |
| Elevators | Interface with other systems (fire alarm, etc) (ASTM testing and certification by others) |
| Escalators | Interface with other systems (fire alarm, etc) (ASTM testing and certification by others) |
| Material Delivery Systems | Interface with other systems (fire alarm, elevators, etc) |
| Pneumatic Tube Systems | Interface with other systems (fire alarm, etc) |
| Fire Suppression |  |
| Fire Pump | Fire Pump, jockey pump, fire pump controller/ATS |
| Fire Sprinkler Systems | Wet pipe system, dry pipe system, pre-action system, special agent systems |
| Plumbing |  |
| Domestic Water Distribution | Booster pumps, backflow preventers, water softeners, potable water storage tanks |
| Domestic Hot Water Systems | Water heaters**, heat exchangers, circulation pumps, point-of-use water heaters* |
| Sewerage Pump Systems | Sewage ejectors |
| Wastewater Pump Systems | Sump pumps |
| Sanitary Waste Interceptors | Grease interceptors, acid neutralizers |
| General Service Air Systems | Packaged compressor systems, air dryers, filtration |
| Medical Air Systems | Packaged medical air compressor units. Outlet certification, cross-connection verification |
| Medical Vacuum Systems | Packaged medical vacuum units, outlet certification, cross-connection verification |
| Dental Air Systems | Packaged dental air compressor units, outlet certification, cross-connect verification |
| Dental Evacuation and Vacuum Systems | Packaged Dental Evacuation units, packaged dental vacuum units, outlet certification, cross-connection verification |
| Waste Anesthesia Gas Systems | Packaged Waste Anesthesia Gas units, outlet certification, cross-connection verification |
| Medical Gas Systems (other than Medical Air Systems) | Medical gas (oxygen, nitrogen, nitrous oxide, etc.) tank/manifold systems, outlet certification, cross-connection verification |
| Chemical Waste Systems | Chemical storage tanks, neutralization systems, ventilation, process control |
| Reverse-Osmosis Systems | Packaged Reverse-Osmosis systems |
| Water De-Alkalizing Systems | Package Water De-Alkalizing systems |
| HVAC |  |
| Noise and Vibration Control | (Noise and vibration levels for critical equipment such as Air Handlers, Chillers, Cooling Towers, Boilers, Generators, etc. will be commissioned as part of the system commissioning) |
| Direct Digital Control System** | Operator Interface Computer, Operator Work Station (including graphics, point mapping, trends, alarms), Network Communications Modules and Wiring, Integration Panels. (DDC Control panels will be commissioned with the systems controlled by the panel) |
| Chilled Water System** | Chillers (centrifugal, rotary screw, air-cooled), pumps (primary, secondary, variable primary), VFDs associated with chilled water system components, DDC Control Panels (including integration with Building Control System) |
| Condenser Water System** | Cooling Towers, Fluid Coolers, heat exchangers/economizers, pumps, VFDs associated with condenser water system components, DDC control panels. |
| Steam/Heating Hot Water System** | Boilers, boiler feed water system, economizers/heat recovery equipment, condensate recovery, water treatment, boiler fuel system, controls, interface with facility DDC system. |
| HVAC Air Handling Systems** | Air handling Units, packaged rooftop AHU, Outdoor Air conditioning units, humidifiers, DDC control panels |
| HVAC Ventilation/Exhaust Systems | General exhaust, toilet exhaust, laboratory exhaust, isolation exhaust, room pressurization control systems |
| HVAC Energy Recovery Systems** | Heat Wheels, Heat Recovery Loops, AHU Integrated Heat Recovery |
| HVAC Terminal Unit Systems** | VAV Terminal Units, CAV terminal units, fan coil units, fin-tube radiation, unit heaters |
| Decentralized Unitary HVAC Systems* | Split-system HVAC systems, controls, interface with facility DDC |
| Unitary Heat Pump Systems** | Water-source heat pumps, controls, interface with facility DDC |
| Humidity Control Systems | Humidifiers, de-humidifiers, controls, interface with facility DDC |
| Hydronic Distribution Systems | Pumps, DDC control panels, heat exchangers, |
| Facility Fuel Systems | Boiler fuel system, generator fuel system |
| Geothermal Energy Direct Use Heating ** | Geothermal well, ground heat exchanger, geothermal pumps, heat exchanger, valves, instrumentation |
| Solar Energy Heating Systems ** | Solar collectors, heat exchangers, storage tanks, solar-boosted domestic hot water heater, pumps, valves, instrumentation |
| Facility Fuel Gas Systems | Witness Natural gas piping pressure testing, natural gas compressors and storage, propane storage |
| Smoke Evacuation System | Atrium smoke evacuation, other smoke evacuation and smoke management systems, controls, interface with other systems (fire alarm), emergency operation. |
| Electrical |  |
| Medium-Voltage Electrical Distribution Systems | Medium-Voltage Switchgear, Medium-Voltage Switches, Underground ductbank and distribution, Pad-Mount Transformers, Medium-Voltage Load Interrupter Switches, |
| Grounding & Bonding Systems | Witness 3rd party testing, review reports |
| Electric Power Monitoring Systems | Metering, sub-metering, power monitoring systems, PLC control systems |
| Electrical System Protective Device Study | Review reports, verify field settings consistent with Study |
| Secondary Unit Substations | Medium-voltage components, transformers, low-voltage distribution, verify breaker testing results (injection current, etc) |
| Low-Voltage Distribution System | Normal power distribution system, Life-safety power distribution system, critical power distribution system, equipment power distribution system, switchboards, distribution panels, panelboards, verify breaker testing results (injection current, etc) |
| Emergency Power Generation Systems | Generators, Generator paralleling switchgear, automatic transfer switches, PLC and other control systems |
| Lighting & Lighting Control** Systems | Emergency lighting, occupancy sensors, lighting control systems, architectural dimming systems, theatrical dimming systems, exterior lighting and controls |
| Cathodic Protection Systems | Review 3rd party testing results. |
| Lightning Protection System | Witness 3rd party testing, review reports |
| Communications |  |
| Grounding & Bonding System | Witness 3rd party testing, review reports |
| Structured Cabling System | Witness 3rd party testing, review reports |
| Master Antenna Television System | Witness 3rd party testing, review reports |
| Public Address & Mass Notification Systems | Witness 3rd party testing, review reports |
| Intercom & Program Systems | Witness 3rd party testing, review reports |
| Nurse Call & Code Blue Systems | Witness 3rd party testing, review reports |
| Security Emergency Call Systems | Witness 3rd party testing, review reports |
| Duress Alarm Systems | Witness 3rd party testing, review reports |
| Electronic Safety and Security |  |
| Grounding & Bonding | Witness 3rd party testing, review reports |
| Physical Access Control Systems | Witness 3rd party testing, review reports |
| Access Control Systems | Witness 3rd party testing, review reports |
| Security Access Detection Systems | Witness 3rd party testing, review reports |
| Video Surveillance System | Witness 3rd party testing, review reports |
| Electronic Personal Protection System | Witness 3rd party testing, review reports |
| Fire Detection and Alarm System | 100% device acceptance testing, battery draw-down test, verify system monitoring, verify interface with other systems. |
| Renewable Energy Sources |  |
| Geothermal Energy Electrical Generation Systems ** | Geothermal well, DC-AC Inverters, storage batteries, turbine generator modules, switchgear, combiner boxes, instrumentation, monitoring and control systems |
| Solar Energy Electrical Power Generation Systems ** | Solar collector modules, DC-AC inverter, storage batteries, combiners, Switchgear, instrumentation, monitoring and control systems |
| Wind Energy Electrical Power Generation Systems ** | Wind Turbines, DC-AC inverter, storage batteries, combiners, switchgear, instrumentation, monitoring and control systems |
| Site Utilities |  |
| Water Utilities | City Water Service Entrance, Backflow Prevention, Pressure Control, Booster Pumps, Irrigation Systems |
| Sanitary Sewerage Utilities | City Sanitary Connection, Waste Treatment Systems |
| Storm Drainage Utilities | City Storm Water Connection, Site Storm Water Distribution |
| Energy Distribution Utilities | Connection to Third Party Energy (Steam, High Temp Hot Water, Chilled Water) Supply Systems, Metering, Pressure Control |
| Transportation |  |
| Active Traffic Barrier Systems | Witness 3rd party testing |
| Integrated Systems Tests |  |
| Loss of Power Response | Loss of power to building, loss of power to campus, restoration of power to building, restoration of power to campus. |
| Fire Alarm Response | Integrated System Response to Fire Alarm Condition and Return to Normal |
| Table Notes |  |
| ** Denotes systems that LEED requires to be commissioned to comply with the Fundamental Commissioning pre-requisite. |  |

## Commissioning Roles and Responsibilities

A.	The following tables outline the roles and responsibilities for the members of the commissioning team during the various phases of the project.  These roles and responsibilities are provided for information and clarification only.  The roles of commissioning team members, other than the Commissioning Agent, are described in other documents (i.e. the Architect/Engineer contract, the Construction contract, the Peer Reviewer contract, etc.)

Editor’s Note:  Edit the following tables to include the specific responsibilities for each Commissioning Team member in the commissioning tasks listed.  The commissioning tasks listed in the Roles and Responsibilities tables should agree with the commissioning tasks included in the commissioning scope of work table.

| Commissioning Team Roles and Responsibilities Design Phase |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Phase | Project Phase/Cx Task (ref Table above for description) | Commissioning Team Member Responsibilities |  |  |  |  |  |
|  |  | VA PM | VA-CFM | VAMC | A/E Team | Commissioning Agent |  |
| Pre-Design | Commissioning Kick Off Meeting | Facilitate the Kick Off Meeting Participate in Kick Off Meeting Provide VA Schedule Requirements and Milestones Review Meeting Minutes & Comment | Identify Cx Team Members Participate in Kick Off Meeting Review Meeting Minutes & Comment | Identify Cx Team Members Participate in Kick Off Meeting Review Meeting Minutes & Comment | Identify Cx Team Members Discuss Design Schedule and Critical Milestones Participate in Kick Off Meeting Review Meeting Minutes & Comment | Prepare and disseminate Agenda Lead Kick Off Meeting Produce Meeting Minutes and Incorporate Comments Prepare Draft Commissioning Plan |  |
| SD-1 | Design Submission Review | Facilitate delivery of Design Submission Documents to Commissioning Agent Review Commissioning Agent Issues Log & provide feedback as appropriate Facilitate resolution of comments by A/E Team | Review Commissioning Agent Issues Log & Provide Feedback as appropriate | Review Commissioning Agent Issues Log & Provide Feedback as appropriate | Deliver Documents to Commissioning Agent for review. Review Dr. Checks comments. Review Commissioning Agent Issues Log Provide Written Responses to Issues | Perform commissioning review and comment on SD1 Design Review submission. Record review comments on Commissioning Issues Log. Incorporate review comments into Dr. Checks. .Record resolution for each issues based on A/E Response; record in Commissioning Issues Log and on Dr. Check. |  |
| SD-1 | Design Narrative | Review Design Narrative & Comment | Review Design Narrative & Comment | Review Design Narrative & Comment | Develop Design Narrative to Include OPR and Basis of Design response to OPR. | Review Design Narrative for compliance with VA Standards and other stated VA Objectives for project. Provide support for developing measurable performance criteria for installed systems. |  |
| SD-1 | Commissioning Plan | Distribute Design Phase Cx Plan Review Cx Plan & Comment | Review Cx Plan & Comment | Review Cx Plan & Comment | Review Cx Plan & Comment | Develop & Submit Project Design Phase Commissioning Plan |  |
| SD-1 | Duration Schedule for Commissioning Activities | Distribute schedule Review and comment | Review and comment | Review and comment | Review schedule and incorporate into project design schedule | Prepare Duration Schedule for Design Phase Commissioning Activities |  |
| SD-1 | Design Review Meeting | Facilitate Design Review Meeting. Facilitate Resolution of Cx Issues | Attend Design Review Meeting as req’d by other VA requirements. | Attend Design Review Meeting | Attend Design Review Meeting. Provide responses to and clarifications of identified Commissioning Issues. | Attend Design Review Meeting. Provide clarification and facilitate resolution to Commissioning Issues Identified |  |
| SD-2 | Design Submission Review | Facilitate delivery of Design Submission Documents to Commissioning Agent Review Commissioning Agent Issues Log & Provide Feedback as appropriate Facilitate Resolution of Comments by A/E Team | Review Commissioning Agent Issues Log & Provide Feedback as appropriate | Review Commissioning Agent Issues Log & Provide Feedback as appropriate | Deliver Documents to Commissioning Agent for review. Review Commissioning Agent Issues Log Provide Written Responses to Issues | Review and comment on SD2 Design Review Log. Provide clarifications as required. Record resolution for each issues based on A/E Response |  |
| SD-2 | Design Narrative | Review Design Narrative & Comment | Review Design Narrative & Provide Feedback as appropriate | Review Design Narrative & Provide Feedback as appropriate | Update Design Narrative to Include OPR and Basis of Design response to OPR. | Review Design Narrative for compliance with VA Standards and other stated VA Objectives for project. Provide support for developing measurable performance criteria for installed systems. |  |
| SD-2 | Commissioning Plan | Distribute Updated Design Phase Cx Plan Review Cx Plan & Comment | Review Cx Plan & Comment | Review Cx Plan & Comment | Review Cx Plan & Comment | Update & Submit Project Commissioning Plan |  |
| SD-2 | Duration Schedule for Commissioning Activities | Distribute schedule Review and comment | Review and comment | Review and comment | Review schedule and incorporate into project design schedule | Update Duration Schedule for Design Phase Commissioning Activities |  |
| SDS-2 | Commissioning Specifications | Review Cx Draft Specs & Comment | Review Cx Draft Specs & Comment | Review Cx Draft Specs & Comment | Incorporate Draft Cx Outline Specifications into Project Submittal. | Review Cx Draft Specs & Comment |  |
| SD-2 | Design Review Meeting | Facilitate Design Review Meeting. Facilitate Resolution of Cx Issues. | Attend Design Review Meeting as required by other VA requirements. Participate in Issue Resolution as appropriate. | Attend Design Review Meeting as required by other VA requirements. Participate in Issue Resolution as appropriate. | Attend Design Review Meeting. Provide responses to and clarifications of identified Commissioning Issues. | Attend Design Review Meeting. Provide clarification and facilitate resolution to Commissioning Issues Identified |  |
| SD-2 | Design Phase Issue Log Resolution | Review & Comment on Revised Design Phase Commissioning Issues Log | Review & Comment on Revised Design Phase Commissioning Issues Log | Review & Comment on Revised Design Phase Commissioning Issues Log | Review & Comment on Revised Design Phase Commissioning Issues Log | Record resolutions to Cx Issues on the Design Phase Commissioning Issues Log. |  |
| DD-1 | Design Submission Review | Facilitate delivery of Design Submission Documents to Commissioning Agent Review Commissioning Agent Issues Log & Provide Feedback as appropriate Facilitate Resolution of Comments by A/E Team | Review Commissioning Agent Issues Log & Provide Feedback as appropriate | Review Commissioning Agent Issues Log & Provide Feedback as appropriate | Deliver Documents to Commissioning Agent for review. Review Commissioning Agent Issues Log Provide Written Responses to Issues | Review and comment on DD1 Design Review Log. Provide clarifications as required. Record resolution for each issues based on A/E Response |  |
| DD-1 | Design Narrative | Review Design Narrative & Comment | Review Design Narrative & Provide Feedback as appropriate | Review Design Narrative & Provide Feedback as appropriate | Update Design Narrative to Include OPR and Basis of Design response to OPR. | Review Design Narrative for compliance with VA Standards and other stated VA Objectives for project. Provide support for developing measurable performance criteria for installed systems. |  |
| DD-1 | Design Phase Controls Meeting | Facilitate and schedule meeting. Participate in meeting | Attend and participate in meeting | Attend and participate in meeting | Chair meeting Attend and participate in meeting | Attend and participate in meeting |  |
| DD-1 | Commissioning Plan | Distribute Updated Design Phase Cx Plan Review Cx Plan & Comment | Review Cx Plan & Comment | Review Cx Plan & Comment | Review Cx Plan & Comment | Update & Project Commissioning Plan |  |
| DD-1 | Duration Schedule for Commissioning Activities | Distribute schedule Review and comment | Review and comment | Review and comment | Review schedule and incorporate into project design schedule | Update Duration Schedule for Design Phase Commissioning Activities Prepare draft duration schedule for Construction Phase Commissioning Activities |  |
| DD-1 | Commissioning Specification | Review Cx Draft Specs & Comment | Review Cx Draft Specs & Comment | Review Cx Draft Specs & Comment | Incorporate Draft Cx Specifications into Project Specification Submittal. Review Cx Draft Specs & Comment | Develop Draft Cx Specifications & Cx Coordination Matrix. Deliver to A/E Team for incorporation into Specification Submittal. |  |
| DD-1 | Design Review Meeting | Facilitate Design Review Meeting. Facilitate Resolution of Cx Issues. | Attend Design Review Meeting as required by other VA requirements. Participate in Issue Resolution as appropriate. | Attend Design Review Meeting as required by other VA requirements. Participate in Issue Resolution as appropriate. | Attend Design Review Meeting. Provide responses to and clarifications of identified Commissioning Issues. | Attend Design Review Meeting. Provide clarification and facilitate resolution to Commissioning Issues Identified |  |
| DD-1 | Design Phase Issue Log Resolution | Review & Comment on Revised Design Phase Commissioning Issues Log | Review & Comment on Revised Design Phase Commissioning Issues Log | Review & Comment on Revised Design Phase Commissioning Issues Log | Review & Comment on Revised Design Phase Commissioning Issues Log | Record resolutions to Cx Issues on the Design Phase Commissioning Issues Log. |  |
| DD-2 | Design Submission Review | Facilitate delivery of Design Submission Documents to Commissioning Agent Review Commissioning Agent Issues Log & Provide Feedback as appropriate Facilitate Resolution of Comments by A/E Team | Review Commissioning Agent Issues Log & Provide Feedback as appropriate | Review Commissioning Agent Issues Log & Provide Feedback as appropriate | Deliver Documents to Commissioning Agent for review. Review Commissioning Agent Issues Log Provide Written Responses to Issues | Review and comment on DD2 Design Review Log. Provide clarifications as required. Record resolution for each issues based on A/E Response |  |
| DD-2 | Design Narrative | Review Design Narrative & Comment | Review Design Narrative & Provide Feedback as appropriate | Review Design Narrative & Provide Feedback as appropriate | Review Updated Design Narrative to Include OPR and Basis of Design response to OPR. | Commissioning Agent to update, review and reconcile the Project Design Narrative. The Design Narrative should reflect the evolution of the project design and note all significant deviations from prior version for ease of review and reconciliation. Design Narrative should describe designer’s response to the project requirements. Where appropriate, provide documentation of approval of deviations from VA Design Criteria and reasoning for same. Provide support for developing measurable performance criteria for installed systems. |  |
| DD-2 | Preliminary Pre-Functional Checklists and Preliminary System Functional Performance Test Procedures | Distribute to Cx Team. Review and comment | None | Review and Comment | Review and Comment | Prepare Preliminary PFC and FPT. Incorporate review comments into the Draft PFCs and FPTs as appropriate. |  |
| DD-2 | Design Phase Controls Meeting | Facilitate and schedule meeting. Participate in meeting | Attend and participate in meeting | Attend and participate in meeting | Chair meeting Attend and participated in meeting | Attend and participate in meeting |  |
| DD-2 | Commissioning Plan | Distribute Updated Design Phase Cx Plan Review Cx Plan & Comment | Review Cx Plan & Comment | Review Cx Plan & Comment | Review Cx Plan & Comment | Update & Submit Project Commissioning Plan |  |
| DD-2 | Commissioning Specification | Review Cx Preliminary Specs & Comment | Review Cx Draft Preliminary & Comment | Review Cx Draft Preliminary & Comment | Incorporate Preliminary Cx Specifications into Project Specification Submittal. Review Cx Draft Specs & Comment | Develop Preliminary Cx Specifications & Cx Coordination Matrix. Deliver to A/E Team for incorporation into Specification Submittal. |  |
| DD-2 | Duration Schedule for Commissioning Activities | Distribute schedule Review and comment | Review and comment | Review and comment | Review schedule and incorporate into project design schedule | Update Duration Schedule for Design Phase Commissioning Activities Update draft duration schedule for Construction Phase Commissioning Activities |  |
| DD-2 | Design Review Meeting | Facilitate Design Review Meeting. Facilitate Resolution of Cx Issues. | Attend Design Review Meeting as required by other VA requirements. Participate in Issue Resolution as appropriate. | Attend Design Review Meeting as required by other VA requirements. Participate in Issue Resolution as appropriate. | Attend Design Review Meeting. Provide responses to and clarifications of identified Commissioning Issues. | Attend Design Review Meeting. Provide clarification and facilitate resolution to Commissioning Issues Identified |  |
| DD-2 | Design Phase Issue Log Resolution | Review & Comment on Revised Design Phase Commissioning Issues Log | Review & Comment on Revised Design Phase Commissioning Issues Log | Review & Comment on Revised Design Phase Commissioning Issues Log | Review & Comment on Revised Design Phase Commissioning Issues Log | Record resolutions to Cx Issues on the Design Phase Commissioning Issues Log. |  |
| CD-1 | Design Submission Review | Facilitate delivery of Design Submission Documents to Commissioning Agent Review Commissioning Agent Issues Log & Provide Feedback as appropriate Facilitate Resolution of Comments by A/E Team | Review Commissioning Agent Issues Log & Provide Feedback as appropriate | Review Commissioning Agent Issues Log & Provide Feedback as appropriate | Deliver Documents to Commissioning Agent for review. Review Commissioning Agent Issues Log Provide Written Responses to Issues | Review and comment on CD1 Design Review Log. Provide clarifications as required. Record resolution for each issues based on A/E Response |  |
| CD-1 | Design Narrative | Review Design Narrative & Comment | Review Design Narrative & Provide Feedback as appropriate | Review Design Narrative & Provide Feedback as appropriate | Review Design Narrative for conformance with current project status. Verify recorded decisions are consistent with Design Team intent and contracts with the VA. | Commissioning Agent to update, review and reconcile the Project Design Narrative. The Design Narrative should reflect the evolution of the project design and note all significant deviations from prior version for ease of review and reconciliation. Design Narrative should describe designer’s response to the project requirements. Where appropriate, provide documentation of approval of deviations from VA Design Criteria and reasoning for same. |  |
| CD-1 | Draft Pre-Functional Checklists and Functional Performance Test procedures | Distribute to team Review and comment | None | Review and Comment | Review and comment | Starting from the Preliminary PFCs and FPTs and review comments, develop Draft PFCx and FPTs. Incorporate into the Construction Phase Commissioning Plan and Commissioning Specifications. |  |
| CD-1 | Design Phase Controls Meeting | Facilitate and schedule meeting. Participate in meeting | Attend and participate in meeting | Attend and participate in meeting | Chair meeting Attend and participated in meeting | Attend and participate in meeting |  |
| CD-1 | Commissioning Plan | Distribute Updated Design Phase Cx Plan Review Cx Plan & Comment | Review Cx Plan & Comment | Review Cx Plan & Comment | Review Cx Plan & Comment | Update & Submit Project Commissioning Plan |  |
| CD-1 | Duration Schedule for Commissioning Activities | Distribute schedule Review and comment | Review and comment | Review and comment | Review schedule and incorporate into project design schedule | Update Duration Schedule for Design Phase Commissioning Activities Update draft duration schedule for Construction Phase Commissioning Activities |  |
| CD-1 | Commissioning Specification | Review Cx Final Specs & Comment | Review Cx Final Specs & Comment | Review Cx Final Specs & Comment | Incorporate Final Cx Specifications into Project Specification Submittal. Review Cx Final Specs & Comment | Develop Final Cx Specifications & Cx Coordination Matrix. Deliver to A/E Team for incorporation into Specification Submittal. |  |
| CD-1 | Design Review Meeting | Facilitate Design Review Meeting. Facilitate Resolution of Cx Issues. | Attend Design Review Meeting as required by other VA requirements. Participate in Issue Resolution as appropriate. | Attend Design Review Meeting as required by other VA requirements. Participate in Issue Resolution as appropriate. | Attend Design Review Meeting. Provide responses to and clarifications of identified Commissioning Issues. | Attend Design Review Meeting. Provide clarification and facilitate resolution to Commissioning Issues Identified |  |
| CD-1 | Design Phase Issue Log Resolution | Review & Comment on Revised Design Phase Commissioning Issues Log | Review & Comment on Revised Design Phase Commissioning Issues Log | Review & Comment on Revised Design Phase Commissioning Issues Log | Review & Comment on Revised Design Phase Commissioning Issues Log | Record resolutions to Cx Issues on the Design Phase Commissioning Issues Log. |  |
| Final | Design Final Design Submission Review | Facilitate delivery of Design Submission Documents to Commissioning Agent Facilitate Resolution of Comments by A/E Team | None | None | Deliver Documents to Commissioning Agent for review. Review Commissioning Agent Issues Log Provide Written Responses to all Outstanding Issues | Review Final Design Submission for resolution of Outstanding Commissioning Issues |  |
| Final | Design Narrative | Review & Approve Final Design Narrative | None | None | Review Design Narrative for conformance with current project status. Verify recorded decisions are consistent with Design Team intent and contracts with the VA. | Commissioning Agent to provide Final Project Design Narrative. The Design Narrative should reflect the evolution of the project design and note all significant deviations from prior version for ease of review and reconciliation. Design Narrative should describe designer’s response to the project requirements. Where appropriate, provide documentation of approval of deviations from VA Design Criteria and reasoning for same. |  |
| Final | Commissioning Plan | Distribute Updated Design Phase Cx Plan Review Cx Plan & Comment | Review Cx Plan & Comment | Review Cx Plan & Comment | Review Cx Plan & Comment | Update & Submit Project Commissioning Plan |  |
| Final | Draft Pre-Functional Checklists and Functional Performance Test procedures | Distribute Review and back-check | None | Review and back-check | Review and back-check | Incorporate back-check comments into the Draft PFCs and FPTs; incorporate into the Commissioning Plan and Final Commissioning Specifications. |  |
| Final | Duration Schedule for Commissioning Activities | Distribute schedule Review and comment | Review and comment | Review and comment | Review schedule and incorporate into project design schedule | Update Duration Schedule for Design Phase Commissioning Activities Update draft duration schedule for Construction Phase Commissioning Activities |  |
| Final | Commissioning Specification | Review Cx Updated Specs & Approve | Review Cx Updated Specs & Comment | Review Cx Updated Specs & Comment | Incorporate Updated Cx Specifications into Project Specification Submittal. | Provide updated Final Cx Specifications & Cx Coordination Matrix. Deliver to A/E Team for incorporation into Specification Submittal. |  |
| Final | Design Phase Issue Log Resolution | Review & Comment on Revised Design Phase Commissioning Issues Log | None | N one | None | Record resolutions to Cx Issues on the Design Phase Commissioning Issues Log. |  |
| Final | Design Phase Commissioning Report | Review, comment and approve | Review and Comment | Review and Comment | Review and Comment | Prepare and submit Design Phase Commissioning Report. |  |

| Commissioning Team Roles and Responsibilities Bid and Pre-Construction Phase |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Phase | Project Phase/Cx Task (ref Table above for description) | Commissioning Team Member Responsibilities |  |  |  |  |
|  |  | VA PM/VA-RE | VA-CFM | VAMC | A/E Team | Commissioning Agent |
| Pre-Bid | Pre Bid Meeting | Organize, schedule and conduct meeting | None | Attend meeting, respond to questions | Attend meeting, respond to questions | Attend meeting, respond to questions |
| Pre-Const. | Pre-Construction Meeting | Organize, schedule and conduct meeting | None | Attend meeting, respond to questions | Attend meeting, respond to questions | Attend meeting, respond to questions |

| Commissioning Team Roles and Responsibilities Construction Phase |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Project Phase/ Cx Task | Commissioning Team Member Responsibilities |  |  |  |  |
|  | VA RE | Commissioning Agent | VAMC | A/E Team | Contractor |
| Commissioning Kick Off Meeting | Facilitate the Kick Off Meeting Provide VA Schedule Requirements and Milestones Review Meeting Minutes & Comment | Prepare and disseminate Agenda Lead Kick Off Meeting Produce Meeting Minutes and Incorporate Comments | Identify Cx Team Members Review Meeting Minutes & Comment | Identify Cx Team Members Review Meeting Minutes & Comment | Identify Cx Team Members (including SC, TAB, DDCC, SpC) Review Meeting Minutes & Comment |
| Duration Schedule for Commissioning Activities | Review Commissioning Agent Duration Schedule and Comment as Appropriate | Refine Commissioning Duration Schedule provided with the specification to include Commissioning Activities, Estimated Duration for each Activity and Conditions Required for Activity Execution | Review Commissioning Agent Duration Schedule and Comment as Appropriate Schedule VAMC Personnel to support Commissioning Process as appropriate | Review Commissioning Agent Duration Schedule and Comment as Appropriate | Review Commissioning Agent Duration Schedule and Comment as Appropriate Incorporate Commissioning Activities into Project CPM Schedule. Confirm with Commissioning Agent |
| Submittal & Shop Drawing Review | Facilitate Delivery of Shop Drawings to Commissioning Agent Review and approve submittals and shop drawings after review by A/E and Commissioning Agent | Provide a list of Required Shop Drawings to CM/GC Review required Shop Drawings in parallel with A/E Team. Deliver Comments to A/E Team as part of Submittal Review Process | None | Review Commissioning Agent Comments Incorporate into A/E Comments as Appropriate Communicate with Commissioning Agent where Cx comments are deemed inappropriate. | Deliver appropriate Shop Drawings to Commissioning Agent when provided to A/E Team. Submittal deliverable must be in contract -Agent address /Section 01340 -in specs? |
| Review RFI’S ASI’S and other Contract Documents | Distribute to CxA | Review documents to identify impacts on Commissioning Process. Review to identify any conflicts with the project OPR. | None | In addition to other contract responsibilities, review and respond to CxA comments. | In addition to other contract responsibilities, review and respond to CxA comments. |
| Project Commissioning Plan | Distribute Design Phase Cx Plan Review Cx Plan & Comment/Approve | Update Project Commissioning Plan to include specific individuals and team members. Update as required for changes in project schedule or work scope as appropriate. | Review Cx Plan & Comment | Review Cx Plan & Comment | Review Cx Plan & Comment Support Construction Team adherence to Cx Plan |
| Site Observations | Review Site Visit Reports and Commissioning Issues Logs and Comment as appropriate. Forward Site Visits Report to Contractor and A/E Facilitate resolution of Commissioning Issues Log Items as expeditiously as possible. | Visit the Project Site on a regular scheduled basis as agreed upon with the VA RE. Submit Site Visit Report to RE. Update and deliver Commissioning Issues Log | Review Site Visit Report & Comment as Appropriate | Review Site Visit Report & Comment as Appropriate Assist the Commissioning Agent in resolving all Design related Commissioning Issues. | Forward Site Visit Report to all Subcontractors, Commissioning Representatives and other appropriate construction team personnel. Review Site Visit Report & Comment as Appropriate Assist the Commissioning Agent in resolving all commissioning Issues. |
| Commissioning Team Meetings | Review Meeting Minutes & Comment | Prepare and disseminate Agenda for regular periodic Cx Team Meetings Lead Cx Team Meetings Produce Meeting Minutes and Incorporate Comments | VAMC Cx Team Members Attend Review Meeting Minutes & Comment | A/E Cx Team Members Attend Review Meeting Minutes & Comment | Cx Team Members (including SC, TAB, DDC, SpC) Attend Review Meeting Minutes & Comment |
| Develop Pre Functional Checklists (PFC’s) | Review & Comment as appropriate | Develop Pre Functional Checklists. (PFC’s) Provide to Contractor for comment. Disseminate final PFC’s for use by Construction Team. | Review & Comment as appropriate | Review & Comment as appropriate | Review & Comment – All Cx Team Members. Incorporate PFC requirements into start up schedules and processes. |
| Develop Functional Performance Test (FPT’s) Procedures | Review & Comment as appropriate | Develop Functional Performance Tests (FPT’s). Provide to Contractor team for comment. Disseminate final FPT’s for use by Construction Team. | Review & Comment as appropriate | Review & Comment as appropriate | Review & Comment – All Cx Team Members. Incorporate FPT requirements into project and personnel schedules. |
| Review Contractor Equipment Startup Checklists, TAB Reports and PFC’s | Review & Comment as appropriate | Review & Comment on result s of Start Up testing, TAB results and PFC documentation. Field Verify a sampling of PFC’s to confirm compliance with PFC requirements. Evaluate readiness for Functional Performance Testing | Review & Comment as appropriate | Review & Comment as appropriate | Provide Factory and Contractor Start Up documentation in accordance with Specifications and PFC’s to VA PM/RE, Commissioning Agent and A/E Team for review & comment. Correct any deficiencies or deviations noted on the Commissioning Issues Log and report corrective action. |
| Review Operations & Maintenance Manuals | Review & Comment on Operations and Maintenance Manuals. | Review & Comment on Operations and Maintenance Manuals. Incorporate into Systems Training as appropriate. | Review & Comment on Operations and Maintenance Manuals. | Review & Comment on Operations and Maintenance Manuals. | Complete & Submit Operations and Maintenance Manuals prior to equipment start up and execution of Pre Functional Checklists. Correct issues identified with O&M Manuals identified on the Commissioning Issues Log. |

| Commissioning Team Roles and Responsibilities Acceptance and Testing Phase |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Project Phase/ Cx Task | Commissioning Team Member Responsibilities |  |  |  |  |
|  | VA RE | Commissioning Agent | VAMC | A/E Team | Contractor |
| Systems Functional Performance Testing | Facilitate execution of the Functional Performance Testing as required. Review Commissioning Agent Issues Log & Provide Feedback as appropriate Facilitate Resolution of Commissioning Issues Log and reporting requirements between the Commissioning Agent and the Construction team. | In collaboration with the Contractor Commissioning Team, direct the execution of the Functional Performance Testing. Identify issues and deficiencies in system operation and performance on the Commissioning Issues Log. Retest systems as appropriate to demonstrate compliance with the Contract Documents and the Commissioning Plan. | Participate with the Commissioning Agent as agreed upon to support the commissioning process and facilitate training of the Operations Team. Review & Comment on Commissioning Issues Log as appropriate. | Review & Comment on the Commissioning Issues Log as appropriate. | Provide Qualified Technicians and Professionals to operate the installed systems and components as required by the Functional Performance Testing and any retesting required by the Commissioning Agent. Provide documentation of test results from installed systems as required by the FPT’s. Correct issues and deficiencies identified on the Commissioning Issues Log and report methods and results of corrective actions to the Commissioning Agent. |
| Prepare Systems Manuals | Review Systems Manual & Approve | Utilizing the accumulated information and data, prepare a Systems Manual for the Operations Team. Review submitted data and note any issues or deficiencies on the Commissioning Issues Log. Deliver Systems Manual to the Cx Team for Review and Comment. | Review Systems Manual & Comment | Provide systems diagrams and other appropriate data to the Commissioning Agent in electronic format for development of Systems Manual. Review Systems Manual & Comment | Provide data, including record drawings and submittal data for all commissioned systems. Correct any deficiencies and issues identified with the submitted data. Review Systems Manual & Comment |
| Training Plan Review | Facilitate Development of Training Agendas and Training Schedules. Review Training Plan & Comment | Facilitate development of Training Agendas. Collaborate with CM/GC/SC and VAMC teams to schedule training activities. Review and Approve all CM/GC/SC training agendas. Note any issues or deficiencies in Agendas on the Commissioning Issues Log. | Review Training Plan & Comment Schedule Appropriate Operations Personnel in accordance with the training schedule. | Review Training Plan & Comment | Develop training agendas in accordance with Project Specifications and submit to Commissioning Agent for review. Coordinate training schedule with Commissioning Agent and other Cx Team members. Schedule and execute training in accordance with training schedule and agendas. |
| Systems Training | Review & Approve Systems Training Agenda Facilitate Systems Training in accordance with the Agenda and Schedule | Develop Systems Training Sessions in accordance with the Commissioning Plan. Sessions shall include the use of the Operations and Maintenance Manual and a ‘Systems Manual’ developed for the VAMC operations Team. Deliver Systems Training in accordance with the approved Systems Training Agenda. | Schedule key O&M Personnel to attend Systems Training Sessions. | Review & Comment on Systems Training Agenda. | Review & Comment on Systems Training Agenda. |
| Final Commissioning Report | Review & Approve Final Commissioning Plan. | Create and submit Final Commissioning Report in accordance with the Commissioning Plan and other contract requirements. | Review & Comment on Final Commissioning Plan | Review & Comment on Final Commissioning Report | None |
| Lessons Learned Review Meeting | Facilitate Lessons Learned Meeting Review & Comment on Meeting Minutes | Distribute the Agenda for the Lessons Learned Meeting. Lead the Lessons Learned Meeting. Complete and distribute Meeting Minutes. Incorporate comments as appropriate. | Attend & Contribute to Meeting. Review & Comment on Meeting Minutes | Attend & Contribute to Meeting. Review & Comment on Meeting Minutes | Attend & Contribute to Meeting. Review & Comment on Meeting Minutes |

| Commissioning Team Roles and Responsibilities Warranty Phase |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Project Phase/ Cx Task | Commissioning Team Member Responsibilities |  |  |  |  |
|  | VA RE | Commissioning Agent | VAMC | A/E Team | Contractor |
| Deferred and/or Seasonal Testing | Facilitate Seasonal Testing with all appropriate parties. Review Commissioning Agent Issues Log & facilitate issues resolution. Facilitate Resolution of identified Commissioning Issues. | Schedule & Execute Seasonal Testing in Accordance with Functional Performance Testing Protocols. Maintain & Distribute Warranty Phase Commissioning Issues Logs. Facilitate and record resolution to identified Issues and Deficiencies recorded on Commissioning Issues Log. | Provide O&M Personnel to support seasonal testing in accordance with the Commissioning Plan. Review Commissioning Agent Issues Log & Comment Operations Team will operate systems under the deferred season testing protocols. | Review & Comment on Seasonal Testing. Provide and report resolution of any issue identified as a Design Issue. | Contractor will be invited to participate in the execution of seasonal testing and assist in resolution of issues and deficiencies identified. Record resolution for each issues based on A/E Response |
| Post-Occupancy Warranty Checkup | Facilitate Post Occupancy Warranty Check Up Meetings. Review and approve Final Commissioning Report Amendment. | Meet with the VAMC Operations Team. Interview team members to evaluate system performance and identify any issues with operation of the commissioned systems. Evaluate system performance through a review of operating performance data and warranty phase (re-commissioning) tests as identified in the Commissioning Plan and Systems Manual. Develop a Warranty Report identifying any outstanding warranty issues for VAMC use in resolving warranty issues on the project. | Provide O&M personnel to participate with the Commissioning Agent in the Post Occupancy Warranty Checkup. Identify any outstanding or persistent warranty issues to the Commissioning Agent. | A/E Team will be invited to participate at their discretion. Review & Comment on Seasonal Testing. Provide and report resolution of any issue identified as a Design Issue. | Contractor will be invited to participate at his discretion. Assist in resolution of issues and deficiencies identified. Assist in facilitating execution of all warranty obligations identified. |
| Final Commissioning Report Amendment | Review & Approve Final Commissioning Report Amendment. | Create and submit Final Commissioning Report Amendment in accordance with the Commissioning Plan and other contract requirements. | Review & Comment on Final Commissioning Report Amendment | Review & Comment on Final Commissioning Report | None |

# Selection Criteria and Weightings

Editor’s Note:  Verify the descending order of importance is appropriate for the project(s).  Edit as necessary.

A.	Proposals will be evaluated and award will be made on the basis of both price and technical considerations most advantageous to the Government as per FAR Part 15.  In descending order of importance, technical evaluations will be based upon firm and Commissioning Agent certifications, experience and qualifications, past performance, capacity, sample work product, and small business participation.  Responsibility determination will be made in accordance with FAR 9.1 Responsible Prospective Contractors.

B.	Technical Evaluations:  All technical factors, when combined, are approximately equal in importance to price.  Evaluations will be based on the following technical weightings in descending order of importance firm and Commissioning Agent certifications is considered more important than experience and qualifications, which is considered more important than past performance, which is considered more important than the commissioning approach, which is considered more important than capacity, which is considered more important that sample work product, which is considered more important than small business, minority-owned business, veteran-owned business, or woman-owned business participation.

1.	Firm and Commissioning Agent Certifications:  Highly qualified offers will be those that clearly demonstrate firm and Commissioning Agent certifications will be based on evidence including:

a.	The firm and/or sub-consulting team member firms are certified by NEBB, ACG, or BCxA.

b.	The Commissioning Agent certification by NEBB, ACG, or BCxA.

2.	Experience and Qualifications will be evaluated based on specialized experience, technical competence, and professional qualifications. Where these sub-factors are of relatively equal importance:

a.	Experience and technical competence:  This sub-factor will be rated on the quality of the firm’s, and its proposed personnel’s, experience.  Highly qualified offers will be those that are well organized and clearly, concisely demonstrate superior experience and technical competence of the firm (or proposed organization, including team sub-consultants) and it key personnel.

Editor’s Note:  Edit the following paragraph to refer to the appropriate section or paragraph of the RFP.  Verify the number of projects, and years of experience agree with the requirements included in prior sections of the RFP.

1)	In providing whole building commissioning services, as described in //section 4.1 Scope of Commissioning Services//, for no less that //four (4) / insert number// healthcare projects completed within the last //five (5) / insert number// years.  Similar size, scope and complexity would include commissioning of new healthcare facility construction, additions to existing healthcare facilities, and/or renovation alteration, maintenance, repair, or upgrades to existing healthcare facilities, sized greater than //200,000 / insert number// square feet with a dollar value in excess of //$100 million / insert dollar value//.

2)	Note:  Experience of prime professionals with sub-consultant team members will not be considered relevant unless each team sub-consultant provides letters committing proposed team for the duration of the project and agreeing to assign to the contract those persons whose resumes, personnel data forms, or personnel qualification statements were submitted.

b	Qualifications:  This sub-factor will be rated on the quality of both the firm’s and its proposed team qualifications.  Highly qualified offers will be those that are well organized and clearly, concisely demonstrate superior qualifications, including:

1).	Evidence that the Commissioning Agent has a minimum of //five (5) / insert years// years’ experience in whole building commissioning projects of similar size, scope, and complexity.

2).	Resumes of all key personnel demonstrating superior education, training, experience, and longevity with the proposed commissioning team.

3).	Superior knowledge and experience of commissioning team members in:

a)	the operation and troubleshooting HVAC, complex electrical systems, and/or open-protocol direct digital control (DDC) systems;

b)	testing, adjusting and balancing (TAB) of HVAC systems;

c)	testing and commissioning building envelopes;

d)	building operations and maintenance;

e)	developing system-level training for O&M personnel;

f)	developing, implementing, and optimizing system control strategies and sequences;

g)	writing and implementing  commissioning plans and functional test procedures;

h)	coordinating commissioning tasks with contractor’s schedules.

4)	Offices within a //100 / insert miles// radius of the project location.

3.	Past Performance:  The assessment of the offeror’s past performance will be used as a means of evaluating the relative capability of the offeror to successfully meet the requirements of the RFP.  The Government reserves the right to obtain information for use in the evaluation of past performance from and all sources, including sources outside the Government.  Offerors lacking relevant past performance history, while rated neutral in past performance, may not represent the most advantageous proposal to the Government and thus, may be an unsuccessful proposal when compared to the proposals of other offerors.  Highly rated offers will be well organized submissions with no less than //three (3) / insert number// current accurate references (including accurate contact information) that clearly and concisely demonstrate superior past performance and client satisfaction with the  commissioning agent with respect to cost control, quality of work, compliance with performance schedules, etc., on no less than //four (4) / insert number// and no more than //four (4) / insert number// projects of similar size, scope, and complexity as that described in this solicitation, completed in the last //five (5) / insert number// years.

4.	Commissioning Approach:  This factor will be evaluated on the offeror’s approach to the commissioning process in terms of conformance to the standards and procedures outlined in the Department of Veterans Affairs, Commissioning Process Manual (available on the Technical Information Library at www.cfm.va.gov/til/).  Highly rated offers will be those that clearly and concisely demonstrate superior understanding of the commissioning process, integrating commissioning tasks into the design and construction process, ability to build an effective commissioning team, quality of work, cost control, compliance with performance schedules, and ability to assist the contractor, design team, and Government with developing and implementing resolution of technical issues identified during the commissioning process.

5.	Capacity:  This factor will be evaluated on the basis of the firm’s (and/or sub-consultant team members’ ability (in terms of labor capacity, operational control, and quality assurance) to perform the project.  Highly rated offers will be those that clearly and concisely demonstrate capacity to perform commissioning for construction projects valued at //$100 million / insert dollar value// or higher and demonstrate superior ability of personnel in key disciplines, equipment availability, and superior management procedures.

6.	Sample Work Product:  This factor will be evaluated on the quality, completeness, and effectiveness of the firm’s sample work product.  Highly rated offers will be well organized, thorough, concise, complete, and recent examples of the proposed team’s work product that demonstrates superior understanding of commissioning processes, control, scheduling, and execution.

7.	Small Business Participation:  This factor will be evaluated on the basis of whether the offeror qualifies as a small business or large business.

a.	Small Business:  A proposal from an offeror that is a small business shall be evaluated on the following, listed in descending order of importance:

1)	Offeror is a Service Disabled Veteran Owned Small Business

2)	Offeror is a Veteran Owned Small Business

3)	Offeror is a Small Business regardless of category.

b.	Large Business:  A proposal from an offeror that is a large business shall be evaluated on the following, listed in descending order of importance:

1)	Offeror is a large business that includes one or more small businesses as part of a teaming arrangement.  Offeror’s proposal will be evaluated on the degree to which the teaming arrangement includes the following, listed in descending order of importance:

a)	Service Disabled Veteran Owned Small Business

b)	Veteran Owned Small Business

c)	Small Business, regardless of category

C.	Price Proposal:  The offeror shall clearly indicate a discount rate from their GSA schedule.  The Discount rate should be applied to all hourly rates listed for the base and options.  Offerors are advised that if the technical proposals are essentially equal, award may be made on the basis of lowest total price for the base and all optional contract line items.  The Government reserves the right to make price/technical tradeoffs that are in the best interest of, or most advantageous to, the Government.  Price will be evaluated on the basis of realism and/or reasonableness, and acceptability to the Government, subject to availability of funds, based on the total price of the base and all options.  The Government’s intent is to award a contract for the base line items and then, solely at its option, based upon availability of funds, exercise each of the optional pre-priced line items for additional services at the time each additional construction contract is awarded.

# Proposal Technical Requirements

## Proposal Deadline

A.	//Insert the date and time proposals are due.  This should be the same date and time identified in paragraph 1.3//

## Proposal Submission Instructions

A.	//Insert identification of the name, address, phone, fax, and email information for the person to receive the proposal.//

B.	//Insert instructions on how may hardcopies and/or electronic copies are required.//

C.	//Insert any information on the page limits, binding instructions, and other administrative instructions for submitting the proposals.//

## Proposal Organization

A.	Provide a cover letter and statement of intent.  Acknowledge receipt of amendments to the RFP.  Indicate acceptance of the contract terms, or identify any exceptions taken to the terms and conditions.

B.	Provide a Technical/Management Proposal organized as follows:

Tab A – Commissioning Firm Information:

1.	Provide the name and location of the proposing firm.  Show locations of all offices and identify the office(s) that will be responsible for the project(s) in this RFP.

2.	Indicate the type of firm (i.e. corporation, sole proprietor, LLC, etc.)

3.	Indicate if the firm is a small business, minority-owned, woman-owned, veteran-owed or other similarly qualified enterprise.

4.	Provide documentation of the firm’s ability to obtain performance bonds.

Tab B – Commissioning Team

1.	Provide an organization chart showing the names and roles of the proposed commissioning agent team.  Include the Principal/Project Executive, Project Manager/Senior Commissioning Agent, key technical leaders (mechanical, electrical, plumbing, fire protection, etc.)

2.	Identify any key sub-consultants and identify their role on the team.

Tab C – Experience and Qualifications

1.	Experience and Technical Competence:

a)	Describe specific relevant experience in Whole Building Commissioning Services.  See Section 3 for qualification requirements.    Projects shall be similar in nature, application and project size.  Firms must address and demonstrate the specialized experience and technical competence of the Commissioning Agent and proposed support team members in each discipline required to address the systems to be commissioned described in Section 4 – Commissioning Services above. For joint venture submittals and prime professionals with sub-consultant team members, each joint venture partner and/or each sub-consultant shall provide letters of commitment to the project team. The offeror agrees to assign to the contract those persons whose resumes, personnel data forms or personnel qualification statements were submitted. If personnel for whatever reason become unavailable for work under the contract for a continuous period exceeding 30 working days, or are expected to devote substantially less effort to the work than indicated in the proposal, the contractor shall propose a substitution of such personnel. All proposed substitutions shall be submitted, in writing, to the Contracting Officer at least 15 days prior to the proposed substitution. All proposed substitutes shall have qualifications equal to or higher than the qualifications of the person being replaced.  Project descriptions should show explicit experience pertinent to this announcement.

2.	Qualifications:

a)	Identify the Project Manager or Senior Commissioning Agent who will be the technical manager and the primary point of contact for day-to-day technical aspects of the project.  Provide resumes and list of related projects.

b)	Identify other key project team members and indicate their role on the Commissioning Team.  Provide resumes and list of related projects.

c)	Provide a Staffing Plan to demonstrate staffing requirements throughout the project.  This Staffing Plan should demonstrate the staffing requirements on a monthly basis throughout the project based on the project schedule information provided in this RFP.

d)	Identify key sub-consultants and previous working experience with the sub-consultants identified in the proposal.  If the offeror is a large business, provide a Sub-Contracting Plan that describes the role and scope of services for proposed sub-consultants.  Identify qualified Service Disabled Veteran-owned, Veteran-Owned, or other small business firms included in the proposal.

Tab D – Past Performance:

1.	Describe the Commissioning Agent firm’s relevant past performance on VA, DOD, GSA, or other projects that are similar with respect to size, scope, complexity, cost control, quality of work and compliance with performance schedules.

2.	Describe the Commissioning Agent firm past performance as the principal commissioning agent for similar healthcare construction projects.  See Section 3 for experience requirements.  Provide contact information for an individual who can provide a reference for at least seven of the ten projects.

3.	For the projects submitted in response to the above requirement, identify the role of the proposed key project personnel including Senior Commissioning Agent or Project Manager, electrical, mechanical communications and envelope Commissioning Specialist.  Indicate if the key individual was an employee or a sub-consultant.

Tab E - Commissioning Approach:

1.	Submit a brief but informative narrative overview of your approach to facilitating and implementing the commissioning services under this contract.  This Commissioning Approach shall be developed in response to this RFP and shall address your project performance ability.  Describe how you will support the scope of services described in Section 4 – Commissioning Services above.  Identify any unique skills, special expertise, and highly-efficient systems, and home office support that will enhance the successful and timely delivery of the services and the project.

2.	The narrative shall include a description of the firm’s ability to manage the commissioning process in coordination with the VA, the A/E, and the Prime Contractor.

3.	The narrative shall include a preliminary schedule for completing commissioning tasks relative to the project schedule data provided in this RFP.

4.	The narrative shall include a discussion of the means and methods to complete the scope of servicers.

5.	The narrative shall also indicate potential challenges or risks that are foreseen along with a plan to mitigate the possible risks or challenges.

Tab F - Capacity:

1.	Describe the Firm’s or Joint Venture’s ability (in terms of labor capacity, operational control and quality assurance) to perform projects with labor fee in the range of approximately $ //insert amount (consistent with maximum contract/task order amount// for the required type in a one-year period. The evaluation will consider the availability of an adequate number of personnel in key disciplines, equipment availability, and demonstrated management procedures.

2.	Describe capacity to execute multiple Task Orders simultaneously while dealing with existing work backlog.

3.	Describe your ability to respond to issues, inquiries, and other requirements in a timely manner.

4.	Provide the location of the firm’s office that will serve the project and demonstrate the proximity of the office relative to the project location.

Tab G – Sample Work Product

1.	Submit examples of the following work products for a recently completed project that were prepared by proposed Commissioning Team members.  Examples should be submitted in electronic PDF format on CD-ROM or DVD:

a.	Commissioning Plan

b.	Commissioning Specifications

c.	Design Review Comments

d.	Field Report for Commissioning Construction Observation Visit

e.	Commissioning Issues Log

f.	Pre-Functional Checklist completed by the contractor

g.	Systems Functional Performance Test Procedure annotated with testing results

h.	Final Commissioning Report (Executive Summary and narrative sections only.)

Tab H – Small Business Participation:

1.	Identify the firm as a large or small business.

2.	If the firm is a small business, identify certifications as a Service Disabled Veteran Owned business, Veteran Owned business, or other category of small business.

3.	If the firm is a large business, identify sub-consultants that are certified as Service Disabled Veteran Owned, business, Veteran Owned business, or other category of small business.  Identify the level of participation (i.e. percentage of scope or percentage of cost) for each sub-consultant.

Tab I - Cost of Services:

1.	Tab I – Cost Of Services shall be submitted in a separate sealed envelope.  Mark the envelope with the Firm Name, RFP Number and Title, and identified as “Tab I – Costs of Service” on the outside of the envelope.