# Domestic Water Heat Exchangers

# Pre-Functional Checklist

| Equipment ID | [Equipment ID] |
| --- | --- |
| Building | [Building] |
| Location | [Room] |

Statement of Readiness

The above equipment and/or systems integral to them are complete and ready for functional testing, except as noted.  None of the outstanding items preclude safe and reliable functional tests being performed.  This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

Responsible Contractor Sign Here

| CONTRACTOR | PRINTED NAME | SIGNATURE | DATE |
| --- | --- | --- | --- |
| General Contractor (GC) |  |  |  |
| Mechanical Contractor (MC) |  |  |  |
| Electrical Contractor (EC) |  |  |  |
| TAB Contractor (TAB) |  |  |  |
| Controls Contractor (CC) |  |  |  |

This statement of readiness has been received by the Commissioning Agent on ___________________ and will be incorporated as part of the final commissioning report.

Equipment Information

| Make |  |  |  | Model Number |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Serial Number |  |  |  | Function |  |  | Service Area |  |  |
| GPM Fluid 1 |  |  |  |  | GPM Fluid 2 |  |  |  |  |
| MBH Fluid 1 |  |  |  |  | MBH Fluid 2 |  |  |  |  |
| Temp In/Out Fluid 1 |  |  |  |  | Temp In/Out Fluid 2 |  |  |  |  |
| Notes: |  |  |  |  |  |  |  |  |  |

System Readiness Checklist

Yes = Checked and Completed, N/A = Not Applicable

| General Installation |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Description |  | Yes | N/A | Initials | Date | Comments |
| General appearance good, no apparent damage |  |  |  |  |  |  |
| Installation is per manufacturers instructions |  |  |  |  |  |  |
| Verified that valves for equipment isolation have been provided per the drawings and specs |  |  |  |  |  |  |
| Record drawings updated to reflect the actual installation |  |  |  |  |  |  |
| Piping, fittings, valves and equipment properly supported and seismically anchored per the details |  |  |  |  |  |  |
| Equipment label permanently affixed |  |  |  |  |  |  |
| Pipes are supported independently of the heat exchanger |  |  |  |  |  |  |
| Provisions in place for expansion compensation |  |  |  |  |  |  |
| Piping, fittings and valves insulated per specification |  |  |  |  |  |  |
| In-line equipment insulated per specification |  |  |  |  |  |  |
| In-line equipment labeled per specification with flows indicated in the correct direction |  |  |  |  |  |  |
| Heat Exchanger pressure tested per manufacturers recommendations |  |  |  |  |  |  |
| Heat Exchanger properly flushed and cleaned per manufacturers recommendations (report attached) |  |  |  |  |  |  |
| Heat exchanger detail checked against the drawings and all devices gages and appurtenances are in place |  |  |  |  |  |  |
| Strainers and low-point drains opened and verified to be clean |  |  |  |  |  |  |
| Construction strainers removed |  |  |  |  |  |  |
| Test plugs (P/T) installed near all control sensors and as per spec |  |  |  |  |  |  |
| Chemical treatment system or plan installed |  |  |  |  |  |  |
| No leaking apparent |  |  |  |  |  |  |
| Air vents and bleeds at high points of systems functional |  |  |  |  |  |  |
| Isolation valves and balancing valves installed |  |  |  |  |  |  |
| Notes: |  |  |  |  |  |  |

| Valves |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Description |  | Yes | N/A | Initials | Date | Comments |
| Isolation valves provided at all branches and main takeoffs to facilitate isolation (as required by contract) |  |  |  |  |  |  |
| Valve installation per manufacturer’s instructions |  |  |  |  |  |  |
| Valve manufacturer labels permanently affixed |  |  |  |  |  |  |
| Manual isolation valves checked for proper seal and operation |  |  |  |  |  |  |
| Valves installed in proper direction |  |  |  |  |  |  |
| Valves stroke fully and easily and spanning is calibrated (see calibration section below) |  |  |  |  |  |  |
| Valves that require a positive shut-off are verified to not be leaking when closed at normal operating pressure |  |  |  |  |  |  |
| No leaking apparent |  |  |  |  |  |  |
| Valves tagged and valve schedule submitted and displayed as required |  |  |  |  |  |  |
| Adequate maintenance clearance in provided and valve is accessible |  |  |  |  |  |  |
| Unions installed to allow for easy removal of control valves |  |  |  |  |  |  |
| Notes: |  |  |  |  |  |  |

| TAB |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Description |  | Yes | N/A | Initials | Date | Comments |
| Installation of system and balancing devices is completed following NEBB or AABC procedures and contract documents |  |  |  |  |  |  |
| Notes: |  |  |  |  |  |  |

Additional Comments: