# Variable-Air Volume Units (Multiple)

# Pre-Functional Checklist

| Equipment ID | [Equipment ID] |
| --- | --- |
| Building | [Building] |
| Location | [Room] |

Statement of Readiness

The above equipment and/or systems integral to them are complete and ready for functional testing, except as noted.  None of the outstanding items preclude safe and reliable functional tests being performed.  This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

Responsible Contractor Sign Here

| CONTRACTOR | PRINTED NAME | SIGNATURE | DATE |
| --- | --- | --- | --- |
| General Contractor (GC) |  |  |  |
| Mechanical Contractor (MC) |  |  |  |
| Electrical Contractor (EC) |  |  |  |
| TAB Contractor (TAB) |  |  |  |
| Controls Contractor (CC) |  |  |  |

This statement of readiness has been received by the Commissioning Agent on ___________________ and will be incorporated as part of the final commissioning report.

Equipment Information

| Make |  |  | Model Number |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Serial Number |  |  | Capacity |  | CFM |  |
| Volts/Phase |  |  | Function |  | Service Area |  |
| Notes: |  |  |  |  |  |  |

| Responsible Contractor | Requirement (Tag numbers based on Mechanical Drawings) | Sign Off | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | AHU- 9 | RTU- 9 | AHU- # | RTU- # | AHU- # | RTU- # | AHU- # | RTU- # | AHU- # | RTU- # | AHU- # | RTU- # | AHU- # | RTU- # | AHU- # | RTU- # |
| Equipment Information |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Make |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Model |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Serial Number |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Capacity |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | CFM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Volts/Phase |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Function |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Service Area |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TAB | Min CFM Setting |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TAB | Max CFM Setting |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| General Installation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Permanent labels affixed to equipment, switches, controls and safety devices. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Each equipment model number complies with approved submittal. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Connection to ductwork is tight and in good condition. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Fan and motor properly installed and operational. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Correct VAV box location is shown on as-built drawings. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Air terminal units are installed level and plumb. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Equipment installation meets serviceability requirements. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Ductwork pressure test has been completed and approved. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Cabinet panels permanently affixed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Thermal insulation has been installed according to specification. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Coils, Piping and Valves |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Dampers are installed and operating properly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Damper operator linkages are tight. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Required length of straight duct provided upstream of air supply terminals. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Manual balancing dampers permanently marked at final setting. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Valve actuators have been fully stroked. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Automatic damper operates full stroke without binding. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Hot water is properly piped to the coil. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Piping is supported by hangers independent of the coil. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Hydrostatic test for re-heat piping complete and report submitted. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Strainers removed and cleaned after system flushing. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Piping insulation complete and undamaged. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Isolation valves are installed, open and accurately located on as-built drawings. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Piping is labeled correctly and flow direction is indicated clearly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | P&T ports have been installed on the inlet and outlet piping of the coil or as indicated in the construction documents. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Coils are clean and fins are in good condition. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Control valves installed as indicated on the document details. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Air vents installed at high points in piping. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | Drain valves installed at low points and have hose connections. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| MC | All piping and accessories installed per contract document details. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Responsible Contractor | Requirement (Tag numbers based on Mechanical Drawings) | Sign Off | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- | VAV --- |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | AHU- 9 | RTU- 9 | AHU- # | RTU- # | AHU- # | RTU- # | AHU- # | RTU- # | AHU- # | RTU- # | AHU- # | RTU- # | AHU- # | RTU- # | AHU- # | RTU- # |
| Testing and Balance |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TAB | Water balancing is complete. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TAB | Air balancing is complete. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TAB | Balancing valves are marked at final setting. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TAB | Dampers are marked at final setting. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TAB | Test and balancing (T&B) report submitted. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TAB | All system pressure and airflow set points have been documented during the test and balance procedure and will be included in the final TAB report. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Electrical and Controls |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| EC | Proper power voltage is supplied. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| EC | Normal power supply energized and identified. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| EC | Control circuit energized and properly identified. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| EC | All control panels are in place. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Control devices have been calibrated and programmed. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Control loops have been tuned in field. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Control damper(s) operator has been fully stroked. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Coil control valve installed and terminated. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Coil control valve powered and calibrated. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Coil control valve is programmed and reads correctly at front end computer. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Operator Workstation - points programmed and generated in graphics. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Discharge temperature sensor installed and accurately located on as-built drawings. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Controls (Sensors I/O) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Analog Inputs |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Zone Temperature |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Zone Setpoint |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Supply #1 CFM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Supply #2 CFM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Supply #3 CFM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Exhaust #1 CFM / snorkel |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Exhaust #2 CFM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Exhaust #3 CFM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Exhaust #4 CFM |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Exhaust #1 Pressure / snorkel |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Exhaust #1 Discharge Air Temp |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Exhaust #2 Discharge Air Temp |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Exhaust #3 Discharge Air Temp |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Analog Outputs |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Supply #1 Air Damper Position |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Supply #2 Air Damper Position |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Supply #3 Air Damper Position |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Exhaust #1 Air Damper Position/Snorkel |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Exhaust #2 Air Damper Position |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Exhaust #3 Air Damper Position |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Exhaust #4 Air Damper Position |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Supply #1 Reheat Valve Position |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Supply #2 Reheat Valve Position |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Supply #3 Reheat Valve Position |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Binary Outputs |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Supply #1 Radiant Panel Valve |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Supply #2 Radiant Panel Valve |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| TCC | Supply #3 Radiant Panel Valve |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

Yes = Checked and Completed, N/A = Not Applicable

Additional Comments: