# Low-Voltage Switchgear – Data Center

# Pre-Functional Checklist

| Equipment ID | [Equipment ID] |
| --- | --- |
| Building | [Building] |
| Location | [Room] |

Statement of Readiness

The above equipment and/or systems integral to them are complete and ready for functional testing, except as noted.  None of the outstanding items preclude safe and reliable functional tests being performed.  This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

Responsible Contractor Sign Here

| CONTRACTOR | PRINTED NAME | SIGNATURE | DATE |
| --- | --- | --- | --- |
| General Contractor (GC) |  |  |  |
| Mechanical Contractor (MC) |  |  |  |
| Electrical Contractor (EC) |  |  |  |
| TAB Contractor (TAB) |  |  |  |
| Controls Contractor (CC) |  |  |  |

This statement of readiness has been received by the Commissioning Agent on ___________________ and will be incorporated as part of the final commissioning report.

EQUIPMENT DATA

Switchgear Nameplate

| Parameter | Data |
| --- | --- |
| Equipment ID |  |
| Manufacturer |  |
| Model |  |
| Type |  |
| Order Number |  |
| Date Manufactured |  |
| Serial Number |  |
| Nominal kVA |  |
| Voltage |  |
| Phase |  |
| Wire |  |
| Continuous Current |  |
| Number of Sections |  |
| Enclosure Type |  |

System Readiness Checklist

Yes = Checked and Completed, N/A = Not Applicable

| Inspection Checklist |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description | Yes | N/A | Initials | Date | Comments |
| As-Built Drawings complete, available and on-site. |  |  |  |  |  |
| Equipment shop drawings available. |  |  |  |  |  |
| Operation and Maintenance manuals available. |  |  |  |  |  |
| Installation and startup manual available. |  |  |  |  |  |
| Equipment warranty information completed and provided in O&M Manual. |  |  |  |  |  |
| Verify receipt and acceptance of manufacturer’s factory test reports. |  |  |  |  |  |
| Doors to electrical room installed. |  |  |  |  |  |
| Locks or temporary security measures installed & operational. Room can be secured. |  |  |  |  |  |
| Electrical room clear of storage, temporary equipment, etc. |  |  |  |  |  |
| Permanent lighting or 30 foot candle temporary lighting in service. |  |  |  |  |  |
| Egress routes from electrical room are unobstructed. |  |  |  |  |  |
| Electrical room & equipment clean of construction debris and dust, and are dry. |  |  |  |  |  |
| Working clearances meet NEC and contract documents. |  |  |  |  |  |
| Equipment has been installed on a level housekeeping pad. |  |  |  |  |  |
| Equipment anchored per manufacturer’s instruction. |  |  |  |  |  |
| Warning Signs installed per shop drawings and contract documents. |  |  |  |  |  |
| All shipped-loose components installed. |  |  |  |  |  |
| Equipment and switchgear grounding and bonding installed for each section. |  |  |  |  |  |
| All grounding connections made with either exothermic process or with non-reversible compression fittings. |  |  |  |  |  |
| Cabinet/compartment doors allow for full swing; latch open and close without binding; and no physical damage. |  |  |  |  |  |
| Bus and units correspond to one-line diagram. |  |  |  |  |  |
| All internal and field wiring completed and switchgear fully assembled. |  |  |  |  |  |
| Interior low voltage switchgear bus and compartments vacuumed and wiped clean with manufacturer approved electrical cleaner. |  |  |  |  |  |
| All bolted connections tightened to their proper torque values. |  |  |  |  |  |
| All wiring installed properly with correct bend radius and no insulation damage. |  |  |  |  |  |
| Testing agency has been scheduled to perform the test and the commissioning agent has been notified of the testing date. |  |  |  |  |  |
| Test equipment requirements have been reviewed with the testing agency. |  |  |  |  |  |
| Power available for test equipment. |  |  |  |  |  |
| Installation is complete and ready for verification testing. |  |  |  |  |  |
| Training Plan approved. |  |  |  |  |  |
| Training sessions of owner training completed / acceptance granted / training materials submitted to Commissioning Agent. |  |  |  |  |  |
| Notes: |  |  |  |  |  |

Additional Comments: