# Switchboards

# Pre-Functional Checklist

| Equipment ID | [Equipment ID] |
| --- | --- |
| Building | [Building] |
| Location | [Room] |

Statement of Readiness

The above equipment and/or systems integral to them are complete and ready for functional testing, except as noted.  None of the outstanding items preclude safe and reliable functional tests being performed.  This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

Responsible Contractor Sign Here

| CONTRACTOR | PRINTED NAME | SIGNATURE | DATE |
| --- | --- | --- | --- |
| General Contractor (GC) |  |  |  |
| Mechanical Contractor (MC) |  |  |  |
| Electrical Contractor (EC) |  |  |  |
| TAB Contractor (TAB) |  |  |  |
| Controls Contractor (CC) |  |  |  |

This statement of readiness has been received by the Commissioning Agent on ___________________ and will be incorporated as part of the final commissioning report.

Equipment Information

| Make |  |  | Model Number |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Serial Number |  |  | NEMA Enclosure |  | KVA |  |
| Volts/Phase |  |  | AMPS |  | KW |  |
| Service Area |  |  |  |  |  |  |
| Notes: |  |  |  |  |  |  |

System Readiness Checklist

Yes = Checked and Completed, N/A = Not Applicable

| General Installation |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description | Yes | N/A | Initials | Date | Comments |
| As-Built Drawings complete |  |  |  |  |  |
| Equipment shop drawings available |  |  |  |  |  |
| Operation and Maintenance manuals available |  |  |  |  |  |
| Installation and startup manual available |  |  |  |  |  |
| Equipment warranty information completed and provided in O&M Manual |  |  |  |  |  |
| Verify receipt and acceptance of manufacturer’s factory test reports |  |  |  |  |  |
| Doors to electrical room installed. |  |  |  |  |  |
| Locks or temporary security measures installed & operational. Room can be secured. |  |  |  |  |  |
| Electrical room clear of storage, temporary equipment, etc. |  |  |  |  |  |
| Permanent lighting or 30 foot candle temporary lighting in service. |  |  |  |  |  |
| Egress routes from electrical room are unobstructed. |  |  |  |  |  |
| Electrical room & equipment clean of construction debris and dust, and are dry. |  |  |  |  |  |
| Working clearances meet NEC and contract documents |  |  |  |  |  |
| Equipment has been installed on a level housekeeping pad. |  |  |  |  |  |
| Equipment anchored per manufacturer’s instruction |  |  |  |  |  |
| Warning Signs installed per shop drawings and contract documents. |  |  |  |  |  |
| All shipped-loose components installed. |  |  |  |  |  |
| Electrical room grounding system complete. |  |  |  |  |  |
| Ground bus(ses) have been installed and terminated to ground system. Grounding electrode connection to building steel completed per design drawings. |  |  |  |  |  |
| Temporary switchboard circuit directory completed. |  |  |  |  |  |
| Component/subsystems are clearly and correctly identified with temporary/permanent labels (bus, section, breakers and devices) |  |  |  |  |  |
| Transient Voltage Suppression System installed per approved shop drawings. |  |  |  |  |  |
| Switchboard labeled with engraved laminated plastic or metal nameplates mounted with corrosion-resistant screws. |  |  |  |  |  |
| Shipping bolts and braces removed |  |  |  |  |  |
| Shipping splits bolted together at proper torque |  |  |  |  |  |
| All enclosure panels and doors in place, fitted & undamaged |  |  |  |  |  |
| All shipped-loose components installed |  |  |  |  |  |
| Current/Potential Transformer fuses are installed and connected. |  |  |  |  |  |
| Verify neutral connection to ground. |  |  |  |  |  |
| All bolted electrical connections have been tightened to their proper torque values. (Note: some connections will be disconnected as part of the FPT. These connections will be field torqued to proper settings at the conclusion of the field-testing.) |  |  |  |  |  |
| All Overcurrent protective devices have been installed at the proper ampere rating and all settings have been adjusted to match the system Coordination Study. |  |  |  |  |  |
| Electrical testing representative has been scheduled to perform the test and the commissioning agent has been notified of the testing date. |  |  |  |  |  |
| Test equipment requirements have been reviewed with electrical testing representative. |  |  |  |  |  |
| Power available for test equipment. |  |  |  |  |  |
| Installation is complete and ready for verification testing. |  |  |  |  |  |
| Training Plan approved |  |  |  |  |  |
| Training sessions of owner training completed / acceptance granted / training materials submitted to Commissioning Agent |  |  |  |  |  |
| Notes: |  |  |  |  |  |

Additional Comments: