Panelboards

# Pre-Functional Checklist

| Equipment ID | [Equipment ID] |
| --- | --- |
| Building | [Building] |
| Location | [Room] |

Statement of Readiness

The above equipment and/or systems integral to them are complete and ready for functional testing, except as noted.  None of the outstanding items preclude safe and reliable functional tests being performed.  This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

Responsible Contractor Sign Here

| CONTRACTOR | PRINTED NAME | SIGNATURE | DATE |
| --- | --- | --- | --- |
| General Contractor (GC) |  |  |  |
| Mechanical Contractor (MC) |  |  |  |
| Electrical Contractor (EC) |  |  |  |
| TAB Contractor (TAB) |  |  |  |
| Controls Contractor (CC) |  |  |  |

This statement of readiness has been received by the Commissioning Agent on ___________________ and will be incorporated as part of the final commissioning report.

Equipment Information

| Make |  |  | Model Number |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Serial Number |  |  | NEMA Enclosure |  | KVA |  |
| Volts/Phase |  |  | AMPS |  | KW |  |
| Service Area |  |  |  |  |  |  |
| Notes: |  |  |  |  |  |  |

System Readiness Checklist

Yes = Checked and Completed, N/A = Not Applicable

| General Installation |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description | Yes | N/A | Initials | Date | Comments |
| As-Built Drawings complete |  |  |  |  |  |
| Equipment shop drawings available |  |  |  |  |  |
| Operation and Maintenance manuals available |  |  |  |  |  |
| Installation and startup manual available |  |  |  |  |  |
| Equipment warranty information completed and provided in O&M Manual |  |  |  |  |  |
| Verify receipt and acceptance of manufacturer’s factory test reports |  |  |  |  |  |
| Verify room, enclosure, and equipment are dry and clean. Building is closed in and sealed to prevent entry of moisture due to weather conditions. |  |  |  |  |  |
| Doors to electrical room installed. |  |  |  |  |  |
| Locks or temporary security measures installed and operational. Room can be secured. |  |  |  |  |  |
| Electrical room clear of storage, temporary equipment, etc. |  |  |  |  |  |
| Permanent lighting or 30 foot candle temporary lighting in service. |  |  |  |  |  |
| Egress routes from electrical room are unobstructed. |  |  |  |  |  |
| Electrical equipment clean of construction debris, dust, and moisture. |  |  |  |  |  |
| Working clearances meet NEC and contract documents |  |  |  |  |  |
| Panelboard has been installed and anchored per manufacturer’s recommendations |  |  |  |  |  |
| Warning Signs installed per shop drawings and contract documents. |  |  |  |  |  |
| Electrical room grounding system complete. |  |  |  |  |  |
| Ground bus(ses) have been installed and terminated to ground system. |  |  |  |  |  |
| Panelboard ratings match one-line drawing. |  |  |  |  |  |
| Temporary panelboard circuit directory completed. |  |  |  |  |  |
| Secondary service, feeder and branch circuit conductors per specifications: - 208/120 V System as follows: - Phase A: Black - Phase B: Red - Phase C: Blue - Neutral: White - Ground: Green - 480/277 V System as follows: - Phase A: Brown - Phase B: Orange - Phase C: Yellow - Neutral: Gray - Ground: Green |  |  |  |  |  |
| Component/subsystems are clearly and correctly identified with temporary/permanent labels (bus, section, breakers and devices) |  |  |  |  |  |
| Panelboard Transient Voltage Suppression System (TVSS) installed per construction and approved shop drawings. |  |  |  |  |  |
| Panelboard labeled with engraved laminated plastic or metal nameplates mounted with corrosion-resistant screws. |  |  |  |  |  |
| Panelboard short circuit rating meets construction and approved shop drawing requirements |  |  |  |  |  |
| Panelboard provided with equipment ground bus per approved shop drawings |  |  |  |  |  |
| Panelboard equipped with shunt trip if applicable per approved shop drawings |  |  |  |  |  |
| Filler plates installed in unused spaces. |  |  |  |  |  |
| Shipping bolts and braces removed |  |  |  |  |  |
| All enclosure panels and doors in place, fitted, undamaged |  |  |  |  |  |
| All shipped-loose components installed |  |  |  |  |  |
| Verify neutral bus isolated from ground. |  |  |  |  |  |
| All bolted electrical connections have been tightened to their proper torque values. |  |  |  |  |  |
| All field connections have been tightened to their proper torque values. |  |  |  |  |  |
| All Overcurrent protective devices have been installed at the proper ampere rating and all settings have been adjusted to match the system Coordination Study. |  |  |  |  |  |
| Operating mechanism of each circuit breaker has been mechanically exercised. |  |  |  |  |  |
| All vent openings are free from obstructions. |  |  |  |  |  |
| Electrical testing representative has been scheduled to perform the test and the commissioning agent has been notified of the testing date. |  |  |  |  |  |
| Test equipment requirements have been reviewed with electrical testing representative. |  |  |  |  |  |
| Power available for test equipment. |  |  |  |  |  |
| Installation is complete and ready for verification testing. |  |  |  |  |  |
| Training Plan approved |  |  |  |  |  |
| Training sessions of owner training completed / acceptance granted / training materials submitted to Commissioning Agent. |  |  |  |  |  |
| Notes: |  |  |  |  |  |

Additional Comments: