# Engine Generators

# Pre-Functional Checklist

| Equipment ID | [Equipment ID] |
| --- | --- |
| Building | [Building] |
| Location | [Room] |

Statement of Readiness

The above equipment and/or systems integral to them are complete and ready for functional testing, except as noted.  None of the outstanding items preclude safe and reliable functional tests being performed.  This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

Responsible Contractor Sign Here

| CONTRACTOR | PRINTED NAME | SIGNATURE | DATE |
| --- | --- | --- | --- |
| General Contractor (GC) |  |  |  |
| Mechanical Contractor (MC) |  |  |  |
| Electrical Contractor (EC) |  |  |  |
| TAB Contractor (TAB) |  |  |  |
| Controls Contractor (CC) |  |  |  |

This statement of readiness has been received by the Commissioning Agent on ___________________ and will be incorporated as part of the final commissioning report.

Equipment Information

| Make |  |  | Model Number |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Serial Number |  |  | NEMA Enclosure |  | KVA |  |
| Volts/Phase |  |  | AMPS |  | KW |  |
| Service Area |  |  |  |  |  |  |
| Notes: |  |  |  |  |  |  |

System Readiness Checklist

Yes = Checked and Completed, N/A = Not Applicable

| General Installation |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description | Yes | N/A | Initials | Date | Comments |
| As-Built drawings complete. |  |  |  |  |  |
| Equipment shop drawings available. |  |  |  |  |  |
| Operation and Maintenance manuals available. |  |  |  |  |  |
| Installation and startup manual available. |  |  |  |  |  |
| Equipment warranty information completed and provided in O&M Manual. |  |  |  |  |  |
| Verify receipt and acceptance of manufacturer’s factory test reports. |  |  |  |  |  |
| Doors to generator room installed. |  |  |  |  |  |
| Locks or temporary security measures installed & operational. Room can be secured. |  |  |  |  |  |
| Generator room clear of storage, temporary equipment, etc. |  |  |  |  |  |
| Permanent lighting or 30 foot candle temporary lighting in service. |  |  |  |  |  |
| Egress routes from generator room are unobstructed. |  |  |  |  |  |
| Generator room & equipment clean of construction debris and dust, and are dry. |  |  |  |  |  |
| Working clearances meet NEC and contract documents. |  |  |  |  |  |
| Equipment has been installed on a level housekeeping pad. |  |  |  |  |  |
| Equipment anchored per manufacturer’s instruction. |  |  |  |  |  |
| Warning signs installed per shop drawings and contract documents. |  |  |  |  |  |
| All shipped-loose components installed. |  |  |  |  |  |
| Electrical room grounding system complete. |  |  |  |  |  |
| Ground bus (ses) have been installed and terminated to ground grid system. |  |  |  |  |  |
| Generator neutral bus is not solidly grounded by factory-installed bonding jumper as specified for a four-pole system. |  |  |  |  |  |
| Generator frame and enclosure bonded to ground. |  |  |  |  |  |
| All wiring installed properly with correct bend radius and no insulation damage. |  |  |  |  |  |
| All power conductors have been braced/tied per manufacturer’s installation instructions. |  |  |  |  |  |
| All piping, electrical, and control connections between skid-mounted devices and non-skid-mounted devices made with flexible connections (pipe, conduit, etc.). |  |  |  |  |  |
| All bolted electrical connections have been tightened to their proper torque values. |  |  |  |  |  |
| Manufacturer’s field service personnel have completed preliminary checkout and startup. |  |  |  |  |  |
| Engine lube oil system is fully operational and free of leaks. |  |  |  |  |  |
| Engine coolant system is fully operational and free of leaks. |  |  |  |  |  |
| Engine fuel supply system is fully operational and free of leaks. |  |  |  |  |  |
| Fuel supply system tank is full and ready for operation. |  |  |  |  |  |
| Engine exhaust is fully operational and free of leaks. |  |  |  |  |  |
| Engine exhaust has rain cap installed at exterior outlet. |  |  |  |  |  |
| Engine exhaust has condensate drain installed at silencer. |  |  |  |  |  |
| Engine exhaust has expansion fitting installed in exhaust piping to account for expansion. |  |  |  |  |  |
| Engine exhaust system, silencer and pipe, are fully insulated. |  |  |  |  |  |
| Intake air and discharge air dampers functional. |  |  |  |  |  |
| Batteries are fully charged and in service. |  |  |  |  |  |
| Battery charger electrically connected to power source and control wiring connections to generator control panel completed. |  |  |  |  |  |
| Generator remote annunciation panel is remotely installed, electrically connected and fully operational. |  |  |  |  |  |
| Generator remote E-stop is remotely installed, electrically connected and fully operational. |  |  |  |  |  |
| Generator control wiring to switchgear installed, electrically connected, and operational with control wiring installed in separate conduit per manufacturer’s recommendations. |  |  |  |  |  |
| Generator control wiring to building management control panel is installed, electrically connected and fully operational. |  |  |  |  |  |
| All contacts, devices, etc. for interface with SCADA-system are installed, functional and wired to terminal strips for connection of field wiring. |  |  |  |  |  |
| Remote annunciator panel is installed, electrically connected and operational. |  |  |  |  |  |
| All circuit breaker protecting devices have been set and recorded per the protective device coordination study. |  |  |  |  |  |
| Metering current transformer ratio and accuracy class matches drawings/specs. |  |  |  |  |  |
| Metering potential transformer ratio and accuracy class matches drawings/specs. |  |  |  |  |  |
| Metering wiring phase and polarity matches meter instruction manual wiring diagrams. |  |  |  |  |  |
| Utility power is available and connected for system operation. |  |  |  |  |  |
| All sensors have been installed and calibrated according to manufacturing and design specification. |  |  |  |  |  |
| All status and alarm indicators are installed and functioning properly. |  |  |  |  |  |
| All field and interconnecting wiring is completed and labeled at each end with visible and readable tags. (Printed markings on the conductors are NOT acceptable.). |  |  |  |  |  |
| Field landed control wiring terminations are made using ring connectors NOT fork connectors. |  |  |  |  |  |
| All manufacturing factory and field start-up tests attached to this SRC. |  |  |  |  |  |
| Testing agency has been scheduled to perform the test and the commissioning agent has been notified of the testing date. |  |  |  |  |  |
| Test equipment requirements have been reviewed with the testing agency. |  |  |  |  |  |
| Power available for test equipment. |  |  |  |  |  |
| Installation is complete and ready for verification testing. |  |  |  |  |  |
| Training plan approved. |  |  |  |  |  |
| Training sessions of owner training completed / acceptance granted / training materials submitted to Commissioning Agent. |  |  |  |  |  |
| All specified tools, equipment & spare parts are on site. |  |  |  |  |  |
| Notes: |  |  |  |  |  |

Additional Comments: