# Automatic Transfer Switches

# Pre-Functional Checklist

| Equipment ID | [Equipment ID] |
| --- | --- |
| Building | [Building] |
| Location | [Room] |

Statement of Readiness

The above equipment and/or systems integral to them are complete and ready for functional testing, except as noted.  None of the outstanding items preclude safe and reliable functional tests being performed.  This checklist does not take the place of the manufacturer’s recommended checkout and startup procedures or report.

Responsible Contractor Sign Here

| CONTRACTOR | PRINTED NAME | SIGNATURE | DATE |
| --- | --- | --- | --- |
| General Contractor (GC) |  |  |  |
| Mechanical Contractor (MC) |  |  |  |
| Electrical Contractor (EC) |  |  |  |
| TAB Contractor (TAB) |  |  |  |
| Controls Contractor (CC) |  |  |  |

This statement of readiness has been received by the Commissioning Agent on ___________________ and will be incorporated as part of the final commissioning report.

EQUIPMENT DATA

Static Switch Nameplate

| Parameter | Data |
| --- | --- |
| Equipment ID |  |
| Manufacturer |  |
| Model |  |
| Catalog Number |  |
| Date Manufactured |  |

Static Switch Source #1 Isolation Circuit Breaker (CB1) Nameplate

| Parameter | Data |
| --- | --- |
| Manufacturer/Model |  |
| Frame Amps |  |
| Volts |  |
| GFI Module |  |
| SC Rating |  |
| Current Rating |  |

Static Switch Source #2 Isolation Circuit Breaker (CB2) Nameplate

| Parameter | Data |
| --- | --- |
| Manufacturer/Model |  |
| Frame Amps |  |
| Volts |  |
| GFI Module |  |
| SC Rating |  |
| Current Rating |  |

Static Switch Output Isolation Circuit Breaker (CB3) Nameplate

| Parameter | Data |
| --- | --- |
| Manufacturer/Model |  |
| Frame Amps |  |
| Volts |  |
| GFI Module |  |
| SC Rating |  |
| Current Rating |  |

Static Switch Bypass to Source #1 Circuit Breaker (CB4) Nameplate

| Parameter | Data |
| --- | --- |
| Manufacturer/Model |  |
| Frame Amps |  |
| Volts |  |
| GFI Module |  |
| SC Rating |  |
| Current Rating |  |

Static Switch Bypass to Source #2 Circuit Breaker (CB5) Nameplate

| Parameter | Data |
| --- | --- |
| Manufacturer/Model |  |
| Frame Amps |  |
| Volts |  |
| GFI Module |  |
| SC Rating |  |
| Current Rating |  |

System Readiness Checklist

Yes = Checked and Completed, N/A = Not Applicable

| Inspection Checklist |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Description | Yes | N/A | Initials | Date | Comments |
| As-Built Drawings complete, available and on-site. |  |  |  |  |  |
| Equipment shop drawings available. |  |  |  |  |  |
| Operation and Maintenance manuals available. |  |  |  |  |  |
| Installation and startup manual available. |  |  |  |  |  |
| Equipment warranty information completed and provided in O&M Manual. |  |  |  |  |  |
| Verify receipt and acceptance of manufacturer’s factory test reports. |  |  |  |  |  |
| Doors to electrical room installed. |  |  |  |  |  |
| Locks or temporary security measures installed & operational. Room can be secured. |  |  |  |  |  |
| Electrical room clear of storage, temporary equipment, etc. |  |  |  |  |  |
| Permanent lighting or 30 foot candle temporary lighting in service. |  |  |  |  |  |
| Egress routes from electrical room are unobstructed. |  |  |  |  |  |
| Electrical room & equipment clean of construction debris and dust, and are dry. |  |  |  |  |  |
| Working clearances meet NEC and contract documents. |  |  |  |  |  |
| Equipment has been installed on a level housekeeping pad or properly attached to the structure or wall. |  |  |  |  |  |
| Equipment anchored per manufacturer’s instruction. |  |  |  |  |  |
| Warning Signs installed per shop drawings and contract documents. |  |  |  |  |  |
| All shipped-loose components installed. |  |  |  |  |  |
| Electrical room grounding system complete. |  |  |  |  |  |
| Grounding electrode conductor has been attached to the building ground ring. |  |  |  |  |  |
| Shipping bolts and braces removed. |  |  |  |  |  |
| ATS doors allow for full swing; latch open and close without binding; and no physical damage. |  |  |  |  |  |
| All field and interconnecting wiring is completed and labeled at each end with visible and readable tags. (Printed markings on the conductors are NOT acceptable.). |  |  |  |  |  |
| All bolted connections tightened to their proper torque values. |  |  |  |  |  |
| All wiring installed properly with correct bend radius and no insulation damage. |  |  |  |  |  |
| All contacts, devices, etc. for interface with SCADA system are installed, functional and wired to terminal strips for connection of field wiring. |  |  |  |  |  |
| Verify Normal and Emergency line side phase rotation. |  |  |  |  |  |
| Verify that NORMAL and EMERGENCY sources are available. |  |  |  |  |  |
| ATS settings have been adjusted per the Engineer/specifications. |  |  |  |  |  |
| Equipment layout and schematic wiring diagrams available and on-site. |  |  |  |  |  |
| System sequence of operation available and on-site. |  |  |  |  |  |
| Remote STS summary alarm wiring complete and tested. |  |  |  |  |  |
| Logic and control connections are routed away from power runs for noise prevention. |  |  |  |  |  |
| Modbus TCP/IP network interface connection made and operational. |  |  |  |  |  |
| Machine room space air conditioning working and available for use. |  |  |  |  |  |
| Factory-supplied critical spare parts inventory delivered and available on-site. |  |  |  |  |  |
| Factory test and startup documentation provided with copies attached to this SRC. |  |  |  |  |  |
| Testing agency has been scheduled to perform the test and the commissioning agent has been notified of the testing date. |  |  |  |  |  |
| Test equipment requirements have been reviewed with the testing agency. |  |  |  |  |  |
| Power available for test equipment. |  |  |  |  |  |
| Installation is complete and ready for verification testing. |  |  |  |  |  |
| Training Plan approved. |  |  |  |  |  |
| Training sessions of owner training completed / acceptance granted / training materials submitted to Commissioning Agent. |  |  |  |  |  |
| Notes: |  |  |  |  |  |

Additional Comments: