# VAV with Reheat

# Functional Performance Test

| Equipment ID | [Equipment ID] |
| --- | --- |
| Building | [Building] |
| Location | [Room] |

## System Description

Description:

Operational Assumptions: All fans are operating. Outside temperature is above 50°F. The system is in occupied mode operation. All of the terminal unit zones used for Unoccupied Mode heating/cooling control is maintaining their occupied space temperature set points within 5°F. Associated Building Automated System (BAS) has been tested and is operating correctly. Trend logging has been initiated.

| Initial Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 1 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 2 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Deferred/Seasonal Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

## Test Participants

| Organization | Required | Optional |
| --- | --- | --- |
| General Contractor |  |  |
| Mechanical Contractor |  |  |
| Electrical Contractor |  |  |
| TAB Contractor |  |  |
| Controls Contractor |  |  |
| Owner’s O&M Personnel |  |  |

## Supplies Required for Testing (To be provided by the contractor)

| Tools / Supplies |  |
| --- | --- |
| Laptop with TC Program | Infrared Thermometer Gun |
| PID Loop Tuning Software | Humidity Tester |
| Aerosol for Smoke and Freeze stat Test | Basic Tool Pouch |
| Radio Communications | Flashlight |

## System Readiness Summary Checklist

| Description | Yes | No | Date |
| --- | --- | --- | --- |
| System Ready for Test |  |  |  |
| Required Personnel Available |  |  |  |
| Required Tools/Test Equipment/Supplies Available |  |  |  |
| Required Safety Equipment Available |  |  |  |

## Set-Points, Limits, and Schedules

AHU can be assigned a schedule.	 Schedule can be programmed daily.

If system runs 24 hours a day, check here. If not, fill in the occupied mode schedule below.

|  | AM |  |  |  |  |  |  |  |  |  |  |  | PM |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Day | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |
| Sun |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Mon |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tues |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Wed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Thurs |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fri |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sat |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Holi |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Parameter | Setpoint |  | Adjustable Range |  |
| --- | --- | --- | --- | --- |
|  | Design | Actual | Design | Actual |
| Outside Air Temperature (°F) |  |  |  |  |
| Preheat valve full open outside air temperature (°F) |  |  |  |  |
| Discharge Air Temperature (°F) |  |  |  |  |
| Night Setback Temperature (°F) |  |  |  |  |
| Night Setback Differential |  |  |  |  |
| Mixed Air Temperature (°F) |  |  |  |  |
| Minimum Start-up Fan Speed (%) |  |  |  |  |
| Time at Minimum Fan Speed for Start-up (min) |  |  |  |  |
| Average Zone Humidity (%RH) |  |  |  |  |
| Maximum supply air humidity (%RH) |  |  |  |  |
| Discharge Air Static Pressure (in H2O) |  |  |  |  |
| High Static Alarm (in H2O) |  |  |  |  |
| Low Static Alarm (in H2O) |  |  |  |  |
| System Shutdown High Static Limit (in H2O) |  |  |  |  |
| Damper Position |  |  |  |  |

## Initial Ambient Conditions

| Ambient Conditions |  |  |  |
| --- | --- | --- | --- |
| Outside Air Temp |  | Outside Air RH % |  |
| Observations |  |  |  |

## Trend Data Required To Support Testing

Check if trend point chart(s) and Frequency Graph(s) are provided per trend requirements shown below.

| Trend Log Setup #1 - Temperature |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Pre-Testing | Post Testing | Point | Frequency | Duration | Provided |
|  |  | System Flow Rate |  |  | Yes No |
|  |  | Flow Rate Set Point |  |  | Yes No |
|  |  | Water Quality |  |  | Yes No |
|  |  | Damper Position |  |  | Yes No |
|  |  | System Pressure |  |  | Yes No |
|  |  | Pressure Set Point |  |  | Yes No |
| Record Issues |  |  |  | Issue Log Item Number: |  |

## Functional Performance Test -- (Verify all components are ready before energizing or operating the system.)

The Commissioning Authority will make and document any changes/addition/deletions to this test procedure required by current system conditions (i.e. weather, system load, utility availability, etc.).

R = Retest (Check () retest required)								Y= Checked and Passed

C = Corrected (Check () when correction verified)					              N = Not Passed

| ACTION |  | REQUIRED REACTION | Y () | N () | COMMENTS |  | R () | C () |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PRE-TEST VISUAL MECHANICAL INSPECTION |  |  |  |  |  |  |  |  |
|  | Ensure all trend information is setup by the controls contractor Record setup values for each VAV box indicate TAB CFME’s | Trend OK. |  |  | Time: _____________(am/pm) |  |  |  |
|  |  | Space temperature. |  |  |  |  |  |  |
|  |  | Space temp set point. |  |  |  |  |  |  |
|  |  | CFM Max Heating. |  |  |  |  |  |  |
|  |  | CFM Min Heating. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Check the operating conditions at the BAS front end and confirm the system is operating automatically under specified sequence. | Occupancy setting corresponds to the occupancy table above. |  |  |  |  |  |  |
|  |  | There are no operator overrides currently on. |  |  |  |  |  |  |
|  |  | No alarm conditions exist. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
| Verification of Temperature Airflow Control – Occupied |  |  |  |  |  |  |  |  |
|  | Adjust thermostat set point to equal current space temperature | Damper goes to minimum position. |  |  |  |  |  |  |
|  |  | Heating valve closed. |  |  |  |  |  |  |
|  |  | Record CFM. |  |  |  |  |  |  |
|  |  | CFM is at minimum per TAB set point. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Adjust the local thermostat set point to be 5°F higher than the current space temperature Wait 3 minutes to record final values | The unit damper remains @ its minimum position (or heating max, if Dual VAV box). |  |  |  |  |  |  |
|  |  | The heating coil control valve modulates open to maintain space temperature set point. |  |  |  |  |  |  |
|  |  | Initial discharge temp. |  |  |  |  |  |  |
|  |  | Final discharge temp. |  |  |  |  |  |  |
|  |  | Heating max CFM. |  |  |  |  |  |  |
|  |  | CFM is at maximum per TAB set point. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Adjust the local thermostat set point to be 5°F lower than the current space temperature Wait 3 minutes to record final value | Unit damper opens fully to max cooling set point (or cooling max if Dual VAV box). |  |  |  |  |  |  |
|  |  | The heating coil control valve is closed. |  |  |  |  |  |  |
|  |  | Initial CFM. |  |  |  |  |  |  |
|  |  | Final CFM. |  |  |  |  |  |  |
|  |  | CFM is at maximum per TAB set point. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Reset the space temperature set point to original value | The unit damper should be in its minimum / normal position. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
| Verification of Unoccupied Mode |  |  |  |  |  |  |  |  |
|  | Put the unit into unoccupied mode | Damper position closed. |  |  |  |  |  |  |
|  |  | Reheat valve closed. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
| Verification of Warm Up and Cool Down Mode |  |  |  |  |  |  |  |  |
|  | Put the unit into warm-up mode | Damper position 100% open. |  |  |  |  |  |  |
|  |  | Temperature set point 71°F. |  |  |  |  |  |  |
|  |  | Reheat valve modulating for heating. |  |  |  |  |  |  |
|  |  | Record CFM. |  |  |  |  |  |  |
|  |  | CFM is at maximum per TAB set point. |  |  |  |  |  |  |
|  |  | Initial discharge temp. |  |  |  |  |  |  |
|  |  | Final discharge temp. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Put the unit into cool down mode | Reheat valve closed. |  |  | *Per controls, 30% is equated with minimum, 100% with maximum |  |  |  |
|  |  | Temperature set point 71°F. |  |  |  |  |  |  |
|  |  | CFM between 30%. |  |  |  |  |  |  |
|  |  | And 100%. |  |  |  |  |  |  |
|  |  | Record CFM. |  |  |  |  |  |  |
|  |  | Initial discharge temp. |  |  |  |  |  |  |
|  |  | Final discharge temp. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Reset the unit into its original settings | Unit returns to its original conditions. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
| Verification of Occupied Mode |  |  |  |  |  |  |  |  |
|  | Put the unit into occupied heating mode | Damper position modulating to maintain temperature. |  |  |  |  |  |  |
|  |  | Temperature set point 71°F. |  |  |  |  |  |  |
|  |  | CFM minimum 30%. |  |  |  |  |  |  |
|  |  | CFM maximum 100%. |  |  |  |  |  |  |
|  |  | Reheat valve modulating for heating when box has reached minimum CFM position. |  |  |  |  |  |  |
|  |  | Reheat valve 100% open box modulating from minimum position to 100% open. |  |  |  |  |  |  |
|  |  | Record CFM Max. |  |  |  |  |  |  |
|  |  | Record CFM set pt. |  |  |  |  |  |  |
|  |  | Record night set pt. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Reset the unit into its original default settings. | System returns to its original default settings. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
| Bypass Mode |  |  |  |  |  |  |  |  |
|  | Put AHU/RTU-__ into VFD bypass mode | VAV damper is fully open. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Return AHU/RTU-___ to normal operation | System operates normally. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
| Return to Initial Conditions |  |  |  |  |  |  |  |  |
|  | Reset the space temperature set-point to the original value | System returns to initial conditions. |  |  |  |  |  |  |
|  |  | Record CFM set pt. |  |  |  |  |  |  |
|  |  | Record temperature set pt. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Record test stop time | Recorded. |  |  | Time: (am / pm) |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |

| ## Final Sign-Off |  |  |  |  |
| --- | --- | --- | --- | --- |
| Commissioning Agent | Printed Name | Initials | Date |  |
| CONTRACTOR | PRINTED NAME | INITIALS | DATE |  |
| General Contractor (GC) |  |  |  |  |
| Mechanical Contractor (MC) |  |  |  |  |
| Electrical Contractor (EC) |  |  |  |  |
| TAB Contractor (TAB) |  |  |  |  |
| Controls Contractor (CC) |  |  |  |  |
| Owner’s O&M Personnel |  |  |  |  |