# Fire Tube Boiler (Low Pressure Steam) System

# Functional Performance Test

| Equipment ID | [Equipment ID] |
| --- | --- |
| Building | [Building] |
| Location | [Room] |

## System Description

Description: Two boilers in penthouse of addition share equipment room with chiller plant addition. The system includes, boilers #7, 8 that expand the capacity of the campus but are not interconnected, Two duplex condensate pumps in boiler room and Mezzanine CRP 3, 4; feed water heat exchanger HX-7; storage tank and feed water pumps BFP 1, 2, 3; and chemical treatment. Low pressure steam is used for humidifiers that are tested with the related air handling equipment, and two heating hot water heat exchangers. The Boilers include various safety sensors, valves, fire controls, and fuel oil pumps considered integral to the boiler operation and tested as part of the boiler. Make up air handling unit 10 provides combustion air and runs when boilers are ON. AHU-10 is tested in a separate FPT. The Fuel Oil Pumps with associated leak detection are tested in a separate FPT. Heat Exchangers HX5, 6 building heating water; and humidifiers are tested on separate FPT’s.

Operational Assumptions:

| Initial Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 1 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 2 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Deferred/Seasonal Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

## Test Participants

| Organization | Required | Optional |
| --- | --- | --- |
| General Contractor |  |  |
| Mechanical Contractor |  |  |
| Electrical Contractor |  |  |
| TAB Contractor |  |  |
| Controls Contractor |  |  |
| Owner’s O&M Personnel |  |  |

## Supplies Required for Testing (To be provided by the contractor)

| Tools / Supplies |  |
| --- | --- |
| Laptop with TC Program | Infrared Thermometer Gun |
| PID Loop Tuning Software | Basic Tool Pouch |
| Radio Communications | Flashlight |

## System Readiness Summary Checklist

| Description | Yes | No | Date |
| --- | --- | --- | --- |
| System readiness checklist completed, approved |  |  |  |
| All control system functions for this and all interlocking systems are programmed and operable per contract documents, including final set-points and schedules with debugging, loop tuning and sensor calibrations completed |  |  |  |
| Punch list items corrected |  |  |  |
| Spot-check system readiness checklist |  |  |  |
| Installation Per Design Documentation & Latest Approved Change Orders |  |  |  |
| O&M Manuals Delivered and Available on Site |  |  |  |
| Field-Marked Copy of As-Built System Schematics Available |  |  |  |
| Specified Contractor’s Test Reports (CTR) Completed |  |  |  |
| Specified Contractor Training of Owner’s Employees Completed |  |  |  |
| Components/Subsystems Clear and Correctly Identified |  |  |  |
| Pumps and piping are properly installed. |  |  |  |

## Set-Points, Limits, and Schedules

AHU can be assigned a schedule.	 Schedule can be programmed daily.

If system runs 24 hours a day, check here. If not, fill in the occupied mode schedule below.

|  | AM |  |  |  |  |  |  |  |  |  |  |  | PM |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Day | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |
| Sun |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Mon |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tues |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Wed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Thurs |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fri |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sat |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Holi |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Parameter | Setpoint |  | Adjustable Range |  |
| --- | --- | --- | --- | --- |
|  | Design | Actual | Design | Actual |
| Boiler Room Space Temp |  |  |  |  |
| Feed Water Temp |  |  |  |  |
| Boiler Steam Pressure St Pt |  |  |  |  |
| Boiler flame purge Delay |  |  |  |  |
| Boiler Pressure Build-up Delay |  |  |  |  |
| Boiler Low Fire De-energize Delay |  |  |  |  |
| Max fire to call for Lag boiler |  |  |  |  |
| Controller High Pressure Limit |  |  |  |  |
| Boiler Lead Lag Schedule |  |  |  |  |
| Exhaust Fan ON Space Temp Exceeds |  |  |  |  |
| Condensate Pump Flow Rate/Pressure |  |  |  |  |
| Feed Water Conductivity St Pt; Hi Limit |  |  |  |  |
| Feed Water Conductivity St Pt; Hi Limit |  |  |  |  |
| Minimum fire rate low load |  |  |  |  |

## Initial Ambient Conditions

| Ambient Conditions |  |  |  |
| --- | --- | --- | --- |
| Outside Air Temp |  | Outside Air RH % |  |
| Observations |  |  |  |

## Trend Data Required To Support Testing

Check if trend point chart(s) and Frequency Graph(s) are provided per trend requirements shown below.

| Trend Log Setup #1 - Temperature |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Pre-Testing | Post Testing | Point | Frequency | Duration | Provided |
|  |  | Boiler #1 On/Off STATUS |  |  | Yes No |
|  |  | Boiler #2 On/Off STATUS |  |  | Yes No |
|  |  | Boiler #1 ALARM STATUS |  |  | Yes No |
|  |  | Boiler #2 ALARM STATUS |  |  | Yes No |
|  |  | Boiler #1 Gas / Oil Fuel Selection STATUS |  |  | Yes No |
|  |  | Boiler #2 Gas / Oil Fuel Selection STATUS |  |  | Yes No |
|  |  | Boiler #1 Supply Pressure or Temp. |  |  | Yes No |
| Record Issues |  |  |  | Issue Log Item Number: |  |

| Trend Log Setup #2 - Temperature |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Pre-Testing | Post Testing | Point | Frequency | Duration | Provided |
|  |  | Make-Up Water Supply Temperature |  |  | Yes No |
|  |  | Boiler #2 Supply Pressure or Temp. |  |  | Yes No |
|  |  | Common Header Pressure / Temperature |  |  | Yes No |
|  |  | Outside Air Temp. |  |  | Yes No |
| Record Issues |  |  |  | Issue Log Item Number: |  |

## Functional Performance Test -- (Verify all components are ready before energizing or operating the system.)

The Commissioning Authority will make and document any changes/addition/deletions to this test procedure required by current system conditions (i.e. weather, system load, utility availability, etc.).

R = Retest (Check () retest required)								Y= Checked and Passed

C = Corrected (Check () when correction verified)					              N = Not Passed

| ACTION |  | REQUIRED REACTION | Y () | N () | COMMENTS |  | R () |  | C () |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ##### PREPARE FOR VERIFICATION TESTING |  |  |  |  |  |  |  |  |  |
|  | Confirm equipment is operating as expected. If not make adjustments with the BAS, Building Automation System. | System is ON and will always have call for heating (includes recovery from loss of power). |  |  | Steam Pressure Common Header _____psi Boiler 7 ____ Boiler 8 _____ AHU-10 is tested in another test procedure. Boilers don’t run if AHU10 OFF Boiler Feedwater Pumps Only run when level is Low and Boiler is ON. They do not run continuously when boiler is ON. |  |  |  |  |
|  |  | System has stable operation. |  |  |  |  |  |  |  |
|  |  | Record common header P. |  |  |  |  |  |  |  |
|  |  | AHU-10 has been commissioned and is operating. |  |  |  |  |  |  |  |
|  |  | AHU-10 is expected to run continuously during normal operation. |  |  |  |  |  |  |  |
|  |  | Only one Boiler is required for existing load. |  |  |  |  |  |  |  |
|  |  | At least one pump of the secondary hot water selection PHWP-4, 5, and 6 is ON. |  |  |  |  |  |  |  |
|  |  | The fuel oil pumps, FOP are OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Confirm that there is always a call for the boilers to run | System is ON and will always have call for heating (includes recovery from loss of power). |  |  | Steam Pressure Common Header _____psi Boiler 7 ____ Boiler 8 _____ AHU-10 is tested in another test procedure. Boilers don’t run if AHU10 OFF Boiler Feedwater Pumps Only run when level is Low and Boiler is ON. They do not run continuously when boiler is ON. |  |  |  |  |
|  |  | System has stable operation. |  |  |  |  |  |  |  |
|  |  | Record common header P. |  |  |  |  |  |  |  |
|  |  | AHU-10 has been commissioned and is operating. |  |  |  |  |  |  |  |
|  |  | AHU-10 is expected to run continuously during normal operation. |  |  |  |  |  |  |  |
|  |  | Only one Boiler is required for existing load. |  |  |  |  |  |  |  |
|  |  | At least one pump of the secondary hot water selection PHWP-4, 5, and 6 is ON. |  |  |  |  |  |  |  |
|  |  | The fuel oil pumps, FOP are OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | If there is actually a very high or low load then adjust RTU outside air or fan VSD CFM so get required loads. | System is ON and will always have call for heating (includes recovery from loss of power). |  |  | Steam Pressure Common Header _____psi Boiler 7 ____ Boiler 8 _____ AHU-10 is tested in another test procedure. Boilers don’t run if AHU10 OFF Boiler Feedwater Pumps Only run when level is Low and Boiler is ON. They do not run continuously when boiler is ON. |  |  |  |  |
|  |  | System has stable operation. |  |  |  |  |  |  |  |
|  |  | Record common header P. |  |  |  |  |  |  |  |
|  |  | AHU-10 has been commissioned and is operating. |  |  |  |  |  |  |  |
|  |  | AHU-10 is expected to run continuously during normal operation. |  |  |  |  |  |  |  |
|  |  | Only one Boiler is required for existing load. |  |  |  |  |  |  |  |
|  |  | At least one pump of the secondary hot water selection PHWP-4, 5, and 6 is ON. |  |  |  |  |  |  |  |
|  |  | The fuel oil pumps, FOP are OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Set fuel selector switch to GAS | System is ON and will always have call for heating (includes recovery from loss of power). |  |  | Steam Pressure Common Header _____psi Boiler 7 ____ Boiler 8 _____ AHU-10 is tested in another test procedure. Boilers don’t run if AHU10 OFF Boiler Feedwater Pumps Only run when level is Low and Boiler is ON. They do not run continuously when boiler is ON. |  |  |  |  |
|  |  | System has stable operation. |  |  |  |  |  |  |  |
|  |  | Record common header P. |  |  |  |  |  |  |  |
|  |  | AHU-10 has been commissioned and is operating. |  |  |  |  |  |  |  |
|  |  | AHU-10 is expected to run continuously during normal operation. |  |  |  |  |  |  |  |
|  |  | Only one Boiler is required for existing load. |  |  |  |  |  |  |  |
|  |  | At least one pump of the secondary hot water selection PHWP-4, 5, and 6 is ON. |  |  |  |  |  |  |  |
|  |  | The fuel oil pumps, FOP are OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Confirm equipment is operating as assumed above. If not make adjustments within the Building Automation System (BAS) | Confirmed. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| ##### VERIFICATION OF BOILER LEAD/LAG OPERATION |  |  |  |  |  |  |  |  |  |
|  | If Lead Lag have a schedule then set it to switch 1 minute from current time | Lead LAG selection changes. |  |  | The boilers have microprocessor controls, but only a manual switch is indicated for lead lag selection. Determine if lead/lag is based only on the manual selection switch or if there is a weekly schedule or runtime hours that could be used? Lead Boiler: B-____ Lag Boiler: B-____ |  |  |  |  |
|  |  | There may be a Message sent to the Operator workstation, OWS to request manual alternating of Boiler LEAD per preset run-time. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | If Lead is made by switch on local panel use it to rotate Lead | Lead LAG selection changes. |  |  | The boilers have microprocessor controls, but only a manual switch is indicated for lead lag selection. Determine if lead/lag is based only on the manual selection switch or if there is a weekly schedule or runtime hours that could be used? Lead Boiler: B-____ Lag Boiler: B-____ |  |  |  |  |
|  |  | There may be a Message sent to the Operator workstation, OWS to request manual alternating of Boiler LEAD per preset run-time. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Note the runtime hours of the lead and lag boiler feed water pumps (BFP) | BFP 1 will run with Boiler 7 and Pump 2 with boiler 8. |  |  | Lead Boiler # _7/ BFP-1 Run time: _____ Lag Boiler # __8/ BFP-2 Run Time: ______ Load: ________MBH The Lead Lag schedule will change during the duration of the following test steps. But the actual firing order of Lead and Lag is expected to remain the same until Both Boilers are OFF. |  |  |  |  |
|  |  | Observe in software that the designation of lead and lag, accumulated runtime assignment and association of pumps are accessible, and modifiable from OWS. This was not clear in specs so an acceptable observation will be NA. |  |  |  |  |  |  |  |
|  |  | Skip any portion of this step not included in the application. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Set the lead Boiler to have 0.5 hours more time than the lag boiler. (or set the Lead Lag scheduler to .5 hours in the future) | BFP 1 will run with Boiler 7 and Pump 2 with boiler 8. |  |  | Lead Boiler # _7/ BFP-1 Run time: _____ Lag Boiler # __8/ BFP-2 Run Time: ______ Load: ________MBH The Lead Lag schedule will change during the duration of the following test steps. But the actual firing order of Lead and Lag is expected to remain the same until Both Boilers are OFF. |  |  |  |  |
|  |  | Observe in software that the designation of lead and lag, accumulated runtime assignment and association of pumps are accessible, and modifiable from OWS. This was not clear in specs so an acceptable observation will be NA. |  |  |  |  |  |  |  |
|  |  | Skip any portion of this step not included in the application. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reduce the settling time and start and stop delay to two minutes. | BFP 1 will run with Boiler 7 and Pump 2 with boiler 8. |  |  | Lead Boiler # _7/ BFP-1 Run time: _____ Lag Boiler # __8/ BFP-2 Run Time: ______ Load: ________MBH The Lead Lag schedule will change during the duration of the following test steps. But the actual firing order of Lead and Lag is expected to remain the same until Both Boilers are OFF. |  |  |  |  |
|  |  | Observe in software that the designation of lead and lag, accumulated runtime assignment and association of pumps are accessible, and modifiable from OWS. This was not clear in specs so an acceptable observation will be NA. |  |  |  |  |  |  |  |
|  |  | Skip any portion of this step not included in the application. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Prepare testing to combine both real loads and flows to provide operational requirements | RTU’s are on and heating valves are open so heat has someplace to go. |  |  | Need to confirm there are no other demands from the other WEAVER LAKE Boilers 1-6 that may call for second boiler to start. This test should only involve B7, 8 lead lag Record temperatures: OAT: ____, Boiler Feed water T ____ Common Supply Steam T__, |  |  |  |  |
|  |  | Outside air dampers are modulated as needed to create loads approximately as required for the various tests steps. |  |  |  |  |  |  |  |
|  |  | Adjust flow to attain loads required for each step. |  |  |  |  |  |  |  |
|  |  | During testing space thermal conditions may not be maintained and AHU/RTU control may need to be modified to allow heating and cooling. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | All existing system boilers B-1 to 6 are ON or “available” but staging is at the B-7, 8 level | RTU’s are on and heating valves are open so heat has someplace to go. |  |  | Need to confirm there are no other demands from the other WEAVER LAKE Boilers 1-6 that may call for second boiler to start. This test should only involve B7, 8 lead lag Record temperatures: OAT: ____, Boiler Feed water T ____ Common Supply Steam T__, |  |  |  |  |
|  |  | Outside air dampers are modulated as needed to create loads approximately as required for the various tests steps. |  |  |  |  |  |  |  |
|  |  | Adjust flow to attain loads required for each step. |  |  |  |  |  |  |  |
|  |  | During testing space thermal conditions may not be maintained and AHU/RTU control may need to be modified to allow heating and cooling. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Operator to command to “OFF” existing boilers if needed to assure the test boilers are the next to operate. | RTU’s are on and heating valves are open so heat has someplace to go. |  |  | Need to confirm there are no other demands from the other WEAVER LAKE Boilers 1-6 that may call for second boiler to start. This test should only involve B7, 8 lead lag Record temperatures: OAT: ____, Boiler Feed water T ____ Common Supply Steam T__, |  |  |  |  |
|  |  | Outside air dampers are modulated as needed to create loads approximately as required for the various tests steps. |  |  |  |  |  |  |  |
|  |  | Adjust flow to attain loads required for each step. |  |  |  |  |  |  |  |
|  |  | During testing space thermal conditions may not be maintained and AHU/RTU control may need to be modified to allow heating and cooling. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Set delay limits and settling time to 1 minute | RTU’s are on and heating valves are open so heat has someplace to go. |  |  | Need to confirm there are no other demands from the other WEAVER LAKE Boilers 1-6 that may call for second boiler to start. This test should only involve B7, 8 lead lag Record temperatures: OAT: ____, Boiler Feed water T ____ Common Supply Steam T__, |  |  |  |  |
|  |  | Outside air dampers are modulated as needed to create loads approximately as required for the various tests steps. |  |  |  |  |  |  |  |
|  |  | Adjust flow to attain loads required for each step. |  |  |  |  |  |  |  |
|  |  | During testing space thermal conditions may not be maintained and AHU/RTU control may need to be modified to allow heating and cooling. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reduce the load slowly | The Lead boiler lowers its firing rate. |  |  | Boiler fire rate is based on rising and falling header pressure. The boiler fails this step if the fire rate cannot turn down to 17%, and remain stable operation. |  |  |  |  |
|  |  | When the fire rate drops to about 17% the boiler steam pressure starts to rise. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Note progressive observations | The Lead boiler lowers its firing rate. |  |  | Boiler fire rate is based on rising and falling header pressure. The boiler fails this step if the fire rate cannot turn down to 17%, and remain stable operation. |  |  |  |  |
|  |  | When the fire rate drops to about 17% the boiler steam pressure starts to rise. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Continue to lower load | When boiler pressure reaches the high safety limit the boiler remains enabled, but stops firing. |  |  | If the run time or scheduler has timed out expect the Lead to change on restart. |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Raise load to original level | Boiler responds to load increase and initiates fire cycle after minimum off delay. |  |  |  |  |  |  |  |
|  |  | Blower purge. |  |  |  |  |  |  |  |
|  |  | Ignition cycle. |  |  |  |  |  |  |  |
|  |  | Fire rate adjustment to load. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Continue to increase Load | Fire rate increases to full fire. |  |  | Pressure in Header when the fire rate increases: _________psi |  |  |  |  |
|  |  | Lag boiler starts with purge, ignition and low fire rate. |  |  |  |  |  |  |  |
|  |  | Lag boiler fire rate increases. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Decrease LOAD | Lag fire rate decreases. |  |  | The boiler fails this step if the fire rate cannot turn down to 17%. |  |  |  |  |
|  |  | Fire rate decreases to 17%. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Decrease the load below upper limit for unload | Lag boiler shuts down. |  |  | Indicate the time required from loss of load to Pump shut down. ___:___ ___:___ ___:___ Boiler off/ Pump Off :/: Delay If liquid level remains high enough the pump will not cycle ON |  |  |  |  |
|  |  | After the Lag boiler proves it is OFF (after 60 seconds) the appropriate Lag feed water pump stops. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Note the time from when the load drops until the boiler pump stops. | Lag boiler shuts down. |  |  | Indicate the time required from loss of load to Pump shut down. ___:___ ___:___ ___:___ Boiler off/ Pump Off :/: Delay If liquid level remains high enough the pump will not cycle ON |  |  |  |  |
|  |  | After the Lag boiler proves it is OFF (after 60 seconds) the appropriate Lag feed water pump stops. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Continue decreasing the load to see that the boiler does shut down. Leave the fire rate at that level. | Lead boiler fire rate decreases. |  |  | Pressure in Header when the fire rate decreases: _________psi The boiler fails this step if the fire rate cannot turn down to 17% and remain stable operation. |  |  |  |  |
|  |  | Lead boiler is enabled but OFF on high steam safety. |  |  |  |  |  |  |  |
|  |  | Lead Boiler changes to Lag if automatic scheduler or runtime Lead alternator is active. |  |  |  |  |  |  |  |
|  |  | Lead Boiler modulates to 17% fire rate. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Create a boiler fault on the lead boiler | The lead boiler stops. |  |  | Pressure in Header when the lag starts: _________psi |  |  |  |  |
|  |  | An alarm is reported, to the OWS. |  |  |  |  |  |  |  |
|  |  | The lag boiler starts. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Note reaction. | The lead boiler stops. |  |  | Pressure in Header when the lag starts: _________psi |  |  |  |  |
|  |  | An alarm is reported, to the OWS. |  |  |  |  |  |  |  |
|  |  | The lag boiler starts. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Restore alarms or faults created in lead boiler. | The Lead boiler restarts. |  |  |  |  |  |  |  |
|  |  | Because the load is low the lag boiler stops. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | SKIP these steps if no auto lead function | The lead boiler (7) changes status to be the “new lag” boiler. |  |  | The specifications do not indicate any other requirement except runtime for the transfer, but if there are others (e.g. both must be off for the run time transfer to be enacted) create those conditions to see the automatic transfer. Hours for switching Lead ____ |  |  |  |  |
|  |  | Boiler (7) shuts down. |  |  |  |  |  |  |  |
|  |  | Boiler (8) starts as the “new lead”. |  |  |  |  |  |  |  |
|  |  | The runtime for the old lead boiler (7) is set to 00:00. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Wait for the lead boiler run time to exceed switch over hours | The lead boiler (7) changes status to be the “new lag” boiler. |  |  | The specifications do not indicate any other requirement except runtime for the transfer, but if there are others (e.g. both must be off for the run time transfer to be enacted) create those conditions to see the automatic transfer. Hours for switching Lead ____ |  |  |  |  |
|  |  | Boiler (7) shuts down. |  |  |  |  |  |  |  |
|  |  | Boiler (8) starts as the “new lead”. |  |  |  |  |  |  |  |
|  |  | The runtime for the old lead boiler (7) is set to 00:00. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Note the automatic transfer of LEAD to become the LAG. This must be verified to be automatic and not a direct command. | The lead boiler (7) changes status to be the “new lag” boiler. |  |  | The specifications do not indicate any other requirement except runtime for the transfer, but if there are others (e.g. both must be off for the run time transfer to be enacted) create those conditions to see the automatic transfer. Hours for switching Lead ____ |  |  |  |  |
|  |  | Boiler (7) shuts down. |  |  |  |  |  |  |  |
|  |  | Boiler (8) starts as the “new lead”. |  |  |  |  |  |  |  |
|  |  | The runtime for the old lead boiler (7) is set to 00:00. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Wait for stable operation of new lead | Alarm Lag boiler ON reports to OWS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Manually turn on the new lag boiler | Alarm Lag boiler ON reports to OWS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Restore “auto” operation to lag boiler | Lag boiler goes OFF. |  |  |  |  |  |  |  |
|  |  | Alarm clears. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Note the conditions after 5 minutes | The system transition is complete and has become stable. |  |  | Record runtimes Boiler # _8 ______ Boiler # __7______ Load: ________MBH |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Adjust the load for one boiler required | The system transition is complete and has become stable. |  |  | Record runtimes Boiler # _8 ______ Boiler # __7______ Load: ________MBH |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| ##### VERIFICATION OF BOILER PRESSURE CONTROL |  |  |  |  |  |  |  |  |  |
|  | Adjust the low fire shutoff delay set point to 1 minute. (Wait 5 minutes for steam pressure to stabilize) | Only the Lead boiler remains on. |  |  | Steam pressure set point ______psi |  |  |  |  |
|  |  | Lag boiler is OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Adjust the steam pressure set point to 5psi higher than the current steam pressure (Wait 5 minutes for steam pressure to stabilize) | The Lead boiler modulates toward full fire. |  |  | Steam pressure set point ________psi |  |  |  |  |
|  |  | The Lag boiler may Start if lead can not provide for load. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Adjust the steam pressure set point to 5psi higher than the current steam pressure set point (Wait 5 minutes for steam pressure to stabilize) | The Lag boiler is enabled. |  |  | Steam pressure set point _______psi |  |  |  |  |
|  |  | After 5 minutes, Lag boiler goes to low fire. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Adjust the steam pressure set point to 5psi* lower than the current set point (Wait 5 minutes for steam pressure to stabilize) | LAG boiler goes to low fire. |  |  | Steam pressure set point _______psi *May need to adjust set point lower in 2 psi increments until low fire is achieved. |  |  |  |  |
|  |  | After 3 minutes at low fire, LAG boiler is de-energized. |  |  |  |  |  |  |  |
|  |  | Lead boiler Reduces from full fire. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Set the Pressuretrol® controller high pressure limit to be 5psi lower than the current pressure | The lead boiler is OFF due to high pressure limit. |  |  | Controller high pressure limit set point _____psi |  |  |  |  |
|  |  | The Lag boiler is enabled. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the steam pressure set point to the original value (10-15 psi) | The boilers resume “normal” operational conditions. |  |  | Steam pressure set point ________psi Low fire time delay set point _____min Controller high pressure limit set point _____psi |  |  |  |  |
|  |  | Wait 5 minutes for steam pressure to stabilize. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the low fire delay to the original setting | The boilers resume “normal” operational conditions. |  |  | Steam pressure set point ________psi Low fire time delay set point _____min Controller high pressure limit set point _____psi |  |  |  |  |
|  |  | Wait 5 minutes for steam pressure to stabilize. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the pressure controller limit to the original value | The boilers resume “normal” operational conditions. |  |  | Steam pressure set point ________psi Low fire time delay set point _____min Controller high pressure limit set point _____psi |  |  |  |  |
|  |  | Wait 5 minutes for steam pressure to stabilize. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| ##### VERIFICATION OF BOILER FAILURE SEQUENCE |  |  |  |  |  |  |  |  |  |
|  | Turn the Lead boiler off locally to simulate failure | The Lead boiler is OFF. |  |  |  |  |  |  |  |
|  |  | The Lag boiler is enabled. |  |  |  |  |  |  |  |
|  |  | After 5 minutes, the Lag boiler begins fire and adjusts to load. |  |  |  |  |  |  |  |
|  |  | An alarm registers at the BAS for lead boiler failure. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Turn the Lag boiler off locally to simulate dual boiler failure | The Lead boiler is OFF. |  |  | Even when there is a call for heating the secondary pumps stop if no boilers are ON. |  |  |  |  |
|  |  | The Lag boiler is OFF. |  |  |  |  |  |  |  |
|  |  | An alarm registers at the BAS for Lag boiler failure. |  |  |  |  |  |  |  |
|  |  | The secondary pumps PHWP 4, 5, 6 stop with second boiler failure. |  |  |  |  |  |  |  |
|  |  | Low header pressure alarm reports to BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Wait for header pressure to drop | The Lead boiler is OFF. |  |  | Even when there is a call for heating the secondary pumps stop if no boilers are ON. |  |  |  |  |
|  |  | The Lag boiler is OFF. |  |  |  |  |  |  |  |
|  |  | An alarm registers at the BAS for Lag boiler failure. |  |  |  |  |  |  |  |
|  |  | The secondary pumps PHWP 4, 5, 6 stop with second boiler failure. |  |  |  |  |  |  |  |
|  |  | Low header pressure alarm reports to BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Restore the Lead boiler fault | The Lead boiler is enabled. |  |  | Verify that when the Lead boiler is brought back on, it resumes Lead role. Is there a time delay before the steam control valve closes on a de-energized boiler? |  |  |  |  |
|  |  | After purge and ignition Lead boiler adjusts fire to meet load. |  |  |  |  |  |  |  |
|  |  | The Lag boiler is OFF. |  |  |  |  |  |  |  |
|  |  | Lead Boiler failure alarm clears at BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Turn the Lag boiler back to ON state | The Lead boiler remains energized. |  |  | Lag Boiler may start if actual line pressure is still low and lead boiler is at full fire. |  |  |  |  |
|  |  | The Lag boiler remains OFF (provided steam pressure set point is met). |  |  |  |  |  |  |  |
|  |  | Lag Boiler failure alarm clears at BAS. |  |  |  |  |  |  |  |
|  |  | System resumes normal operation. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| ##### VERIFICATION OF BOILER FEED WATER PUMPS, SAFETY CIRCUIT AND ALARMS |  |  |  |  |  |  |  |  |  |
|  | Boiler Feedwater Pump Observe during normal operation low water level on Lead Boiler 7 | Boiler fed water pump BFP-1 starts for B-7. |  |  |  |  |  |  |  |
|  |  | Make up water solenoid valve opens as feed water tank water level falls. |  |  |  |  |  |  |  |
|  |  | Steam valve for HX-7 opens to maintain feed water temperature. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Change Lead boiler to boiler 8 | Boiler fed water pump BFP-2 starts for B-8. |  |  |  |  |  |  |  |
|  |  | Make up water solenoid valve opens as feed water tank water level falls. |  |  |  |  |  |  |  |
|  |  | Steam valve for HX-8 opens to maintain feed water temperature. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Observe during normal operation low water level on Lead Boiler 8 | Boiler fed water pump BFP-2 starts for B-8. |  |  |  |  |  |  |  |
|  |  | Make up water solenoid valve opens as feed water tank water level falls. |  |  |  |  |  |  |  |
|  |  | Steam valve for HX-8 opens to maintain feed water temperature. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Manually stop BFP 2 | Boiler fed water pump BFP-3 starts for B-8 low water call for make up. |  |  | Confirm that valve setup would allow BFP-3 to also serve Boiler 7. |  |  |  |  |
|  |  | Boiler B-8 is served with water and fills for normal operation. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Manually enable BFP3 to run with boiler | Boiler fed water pump BFP-3 starts for B-8 low water call for make up. |  |  | Confirm that valve setup would allow BFP-3 to also serve Boiler 7. |  |  |  |  |
|  |  | Boiler B-8 is served with water and fills for normal operation. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Manually adjust valves so BFP 3 delivers water to Boiler-8 | Boiler fed water pump BFP-3 starts for B-8 low water call for make up. |  |  | Confirm that valve setup would allow BFP-3 to also serve Boiler 7. |  |  |  |  |
|  |  | Boiler B-8 is served with water and fills for normal operation. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Observe action on low water on Boiler 8 | Boiler fed water pump BFP-3 starts for B-8 low water call for make up. |  |  | Confirm that valve setup would allow BFP-3 to also serve Boiler 7. |  |  |  |  |
|  |  | Boiler B-8 is served with water and fills for normal operation. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Return BFP-3 to standby and valve BFP-2 as service for B-8 | BFP-2 provides makeup water for boiler 8. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Return BFP-2 to serve B-8. | BFP-2 provides makeup water for boiler 8. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Boiler Safety Water Level With Boiler 7 as lead boiler and with a load for one boiler complete the following section for Boiler B-7. | The controller starts low water level sequence. |  |  |  |  |  |  |  |
|  |  | The feed water pump STARTS. |  |  |  |  |  |  |  |
|  |  | As water level drops further the LOW alarm trips. |  |  |  |  |  |  |  |
|  |  | The burner circuit is open and the burners shut OFF. |  |  |  |  |  |  |  |
|  |  | A local alarm is sounded. |  |  |  |  |  |  |  |
|  |  | A general alarm is registered at the BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Boiler Safety Water Level Blow down the boiler column to a point that trips the low-level switch. | The controller starts low water level sequence. |  |  |  |  |  |  |  |
|  |  | The feed water pump STARTS. |  |  |  |  |  |  |  |
|  |  | As water level drops further the LOW alarm trips. |  |  |  |  |  |  |  |
|  |  | The burner circuit is open and the burners shut OFF. |  |  |  |  |  |  |  |
|  |  | A local alarm is sounded. |  |  |  |  |  |  |  |
|  |  | A general alarm is registered at the BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Boiler Safety Water Level Limit boiler feed water to assure it does not fill faster than blow down | The controller starts low water level sequence. |  |  |  |  |  |  |  |
|  |  | The feed water pump STARTS. |  |  |  |  |  |  |  |
|  |  | As water level drops further the LOW alarm trips. |  |  |  |  |  |  |  |
|  |  | The burner circuit is open and the burners shut OFF. |  |  |  |  |  |  |  |
|  |  | A local alarm is sounded. |  |  |  |  |  |  |  |
|  |  | A general alarm is registered at the BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Water fills the boiler back to acceptable level | The boiler resumes “normal” operating sequence. |  |  |  |  |  |  |  |
|  |  | The local alarm is cleared. |  |  |  |  |  |  |  |
|  |  | The general alarm clears at the BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Fuel oil Set fuel mode switch to “oil” | FOP-1 starts when the selector is set to oil. |  |  | There may be a report sent to BAS that the system in OIL mode, and that FOP1 is ON. |  |  |  |  |
|  |  | FO is delivered to the boiler by FOP1. |  |  |  |  |  |  |  |
|  |  | Local control shows FOP-1 ON. |  |  |  |  |  |  |  |
|  |  | Boiler fires. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Fuel oil Set FOP-1 to Lead | FOP-1 starts when the selector is set to oil. |  |  | There may be a report sent to BAS that the system in OIL mode, and that FOP1 is ON. |  |  |  |  |
|  |  | FO is delivered to the boiler by FOP1. |  |  |  |  |  |  |  |
|  |  | Local control shows FOP-1 ON. |  |  |  |  |  |  |  |
|  |  | Boiler fires. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Fuel oil Allow ether boiler to start | FOP-1 starts when the selector is set to oil. |  |  | There may be a report sent to BAS that the system in OIL mode, and that FOP1 is ON. |  |  |  |  |
|  |  | FO is delivered to the boiler by FOP1. |  |  |  |  |  |  |  |
|  |  | Local control shows FOP-1 ON. |  |  |  |  |  |  |  |
|  |  | Boiler fires. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Simulate a fault in FOP-1 | FOP-1 stops. |  |  | If possible trip a pump overload, to trigger alarm and shutdown. The thermal overload is a unique alarm and reports locally and to BAS There may be a 30 second delay before the Lag pump starts. |  |  |  |  |
|  |  | An alarm reports locally. |  |  |  |  |  |  |  |
|  |  | An alarm FOP 1 Failure reports to BAS. |  |  |  |  |  |  |  |
|  |  | FOP-2 starts. |  |  |  |  |  |  |  |
|  |  | The boiler continues to run. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Simulate a fault in FOP-2 | FOP-2 stops. |  |  | Boiler may need a manual reset if SO record procedure here: The loss of flow alarm is a unique alarm that reports locally and at BAS. |  |  |  |  |
|  |  | An alarm reports locally. |  |  |  |  |  |  |  |
|  |  | An alarm FOP 2 Failure reports to BAS. |  |  |  |  |  |  |  |
|  |  | Boiler shuts down. |  |  |  |  |  |  |  |
|  |  | Low FO Flow Alarm reports to BAS after 30 seconds. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Shut off circuit to controller for 10 seconds to simulate a loss of power, then turn back ON | Controller recovers from loss of power and automatically restarts. |  |  | The controller may report a return from loss of power alarm. |  |  |  |  |
|  |  | FOP-1 starts. |  |  |  |  |  |  |  |
|  |  | The Local and BAS alarms for FOP-1 clear. |  |  |  |  |  |  |  |
|  |  | Boiler starts. |  |  |  |  |  |  |  |
|  |  | FO Flow Alarm Clears at BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Correct Simulated fault in FOP-1 | Controller recovers from loss of power and automatically restarts. |  |  | The controller may report a return from loss of power alarm. |  |  |  |  |
|  |  | FOP-1 starts. |  |  |  |  |  |  |  |
|  |  | The Local and BAS alarms for FOP-1 clear. |  |  |  |  |  |  |  |
|  |  | Boiler starts. |  |  |  |  |  |  |  |
|  |  | FO Flow Alarm Clears at BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Manually acknowledge alarm by depressing “reset” button | Controller recovers from loss of power and automatically restarts. |  |  | The controller may report a return from loss of power alarm. |  |  |  |  |
|  |  | FOP-1 starts. |  |  |  |  |  |  |  |
|  |  | The Local and BAS alarms for FOP-1 clear. |  |  |  |  |  |  |  |
|  |  | Boiler starts. |  |  |  |  |  |  |  |
|  |  | FO Flow Alarm Clears at BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Correct Simulated fault in FOP-2 | FOP-2 remains OFF as LAG. |  |  |  |  |  |  |  |
|  |  | The Local and BAS alarms for FOP-2 clear. |  |  |  |  |  |  |  |
|  |  | Boiler remains ON. |  |  |  |  |  |  |  |
|  |  | After Lead selection is changed FOP 2 Starts. |  |  |  |  |  |  |  |
|  |  | FOP-1 Stops. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Manually acknowledge alarm by depressing “reset” button | FOP-2 remains OFF as LAG. |  |  |  |  |  |  |  |
|  |  | The Local and BAS alarms for FOP-2 clear. |  |  |  |  |  |  |  |
|  |  | Boiler remains ON. |  |  |  |  |  |  |  |
|  |  | After Lead selection is changed FOP 2 Starts. |  |  |  |  |  |  |  |
|  |  | FOP-1 Stops. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Use a small amount of fuel to bridge the contacts on the leak detector (or lift float if that is the sensor type) in the outer fuel tank. | Alarm sounds locally. |  |  | This is a unique pump set leak alarm that reports locally and at BAS. |  |  |  |  |
|  |  | BAS reports Alarm. |  |  |  |  |  |  |  |
|  |  | In addition a pipe leak stops the system and Both Pumps are OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Use water or fuel to close contact on pipe leak detector. | Alarm sounds locally. |  |  | This is a unique pump set leak alarm that reports locally and at BAS. |  |  |  |  |
|  |  | BAS reports Alarm. |  |  |  |  |  |  |  |
|  |  | In addition a pipe leak stops the system and Both Pumps are OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Change fuel Mode switch to “GAS” | FOP-2 Stops. |  |  |  |  |  |  |  |
|  |  | The BAS and Local control show System in GAS fuel mode. |  |  |  |  |  |  |  |
|  |  | Boiler remains ON. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Boiler Safety Flame Detection Disconnect the lead to the flame sensor from the control board | The controller senses no flame. |  |  |  |  |  |  |  |
|  |  | The gas valve closes as a safety. |  |  |  |  |  |  |  |
|  |  | The local control alarms. |  |  |  |  |  |  |  |
|  |  | A general alarm registers at the BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reconnect the lead to the flame sensor | The boiler begins startup sequence. |  |  | On restart the boiler lead lag may reverse. Report actual reaction. |  |  |  |  |
|  |  | The boiler is ON. |  |  |  |  |  |  |  |
|  |  | The local alarm clears. |  |  |  |  |  |  |  |
|  |  | The general alarm at the BAS clears. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the boiler if not recycling be itself | The boiler begins startup sequence. |  |  | On restart the boiler lead lag may reverse. Report actual reaction. |  |  |  |  |
|  |  | The boiler is ON. |  |  |  |  |  |  |  |
|  |  | The local alarm clears. |  |  |  |  |  |  |  |
|  |  | The general alarm at the BAS clears. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Boiler Safety Water Level Change boiler 8 to Lead | The controller starts low water level sequence. |  |  |  |  |  |  |  |
|  |  | The feed water pump STARTS. |  |  |  |  |  |  |  |
|  |  | As water level drops further the LOW alarm trips. |  |  |  |  |  |  |  |
|  |  | The burner circuit is open and the burners shut OFF. |  |  |  |  |  |  |  |
|  |  | A local alarm is sounded. |  |  |  |  |  |  |  |
|  |  | A general alarm is registered at the BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Boiler Safety Water Level With Boiler 8 as lead boiler and with a load for one boiler complete the following section for Boiler B-8. | The controller starts low water level sequence. |  |  |  |  |  |  |  |
|  |  | The feed water pump STARTS. |  |  |  |  |  |  |  |
|  |  | As water level drops further the LOW alarm trips. |  |  |  |  |  |  |  |
|  |  | The burner circuit is open and the burners shut OFF. |  |  |  |  |  |  |  |
|  |  | A local alarm is sounded. |  |  |  |  |  |  |  |
|  |  | A general alarm is registered at the BAS |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Boiler Safety Water Level Blow down the boiler column to a point that trips the low-level switch. | The controller starts low water level sequence. |  |  |  |  |  |  |  |
|  |  | The feed water pump STARTS. |  |  |  |  |  |  |  |
|  |  | As water level drops further the LOW alarm trips. |  |  |  |  |  |  |  |
|  |  | The burner circuit is open and the burners shut OFF. |  |  |  |  |  |  |  |
|  |  | A local alarm is sounded. |  |  |  |  |  |  |  |
|  |  | A general alarm is registered at the BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Boiler Safety Water Level Limit boiler feed water to assure it does not fill faster than blow down | The controller starts low water level sequence. |  |  |  |  |  |  |  |
|  |  | The feed water pump STARTS. |  |  |  |  |  |  |  |
|  |  | As water level drops further the LOW alarm trips. |  |  |  |  |  |  |  |
|  |  | The burner circuit is open and the burners shut OFF. |  |  |  |  |  |  |  |
|  |  | A local alarm is sounded. |  |  |  |  |  |  |  |
|  |  | A general alarm is registered at the BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | (Self Acting) Water fills the boiler back to acceptable level | The boiler resume “normal” operating sequence. |  |  |  |  |  |  |  |
|  |  | The local alarm is cleared. |  |  |  |  |  |  |  |
|  |  | The general alarm clears at the BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Boiler Safety Flame Detection Disconnect the lead to the flame sensor from the control board | The controller senses no flame. |  |  |  |  |  |  |  |
|  |  | The gas valve closes as a safety. |  |  |  |  |  |  |  |
|  |  | The local control alarms. |  |  |  |  |  |  |  |
|  |  | A general alarm registers at the BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reconnect the lead to the flame sensor | The boiler begins startup sequence. |  |  | On restart the boiler lead lag may reverse. Report actual reaction. |  |  |  |  |
|  |  | The boiler is ON. |  |  |  |  |  |  |  |
|  |  | The local alarm clears. |  |  |  |  |  |  |  |
|  |  | The general alarm at the BAS clears. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the boiler if not recycling be itself | The boiler begins startup sequence. |  |  | On restart the boiler lead lag may reverse. Report actual reaction. |  |  |  |  |
|  |  | The boiler is ON. |  |  |  |  |  |  |  |
|  |  | The local alarm clears. |  |  |  |  |  |  |  |
|  |  | The general alarm at the BAS clears |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Set-up Complete the following section that applies to both boilers. | Common safety circuits apply to both boilers regardless of LEAD. |  |  | Confirm in software that the common shut down safeties, alarm reporting and restart apply to both boilers. |  |  |  |  |
|  |  | Neither boiler runs when a common safety is energized. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Boiler Safety – Boiler Emergency Shut OFF Activate the Emergency Shut OFF Switch | The controller looses all power. |  |  | It was not clear on loss of power to boiler control if any staged or planned shutdown would apply. Without a controller there is not timer to delay any shut down action. Without power the alarm identification may be loss of communications, and after time a low boiler system pressure. Record observed or expected results per Software. |  |  |  |  |
|  |  | The gas valve closes as a safety. |  |  |  |  |  |  |  |
|  |  | The Boiler begins shut down cycle. |  |  |  |  |  |  |  |
|  |  | The local control alarms. |  |  |  |  |  |  |  |
|  |  | A loss of power alarm registers at the BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Restore the Emergency Shut OFF switch | The boiler begins startup sequence. |  |  |  |  |  |  |  |
|  |  | The boiler is ON. |  |  |  |  |  |  |  |
|  |  | The local alarm clears. |  |  |  |  |  |  |  |
|  |  | The general alarm at the BAS clears. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the boiler if not recycling be itself | The boiler begins startup sequence. |  |  |  |  |  |  |  |
|  |  | The boiler is ON. |  |  |  |  |  |  |  |
|  |  | The local alarm clears. |  |  |  |  |  |  |  |
|  |  | The general alarm at the BAS clears. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Boiler Safety – Combustion Air Failure Manipulate the AHU-10 damper end switch to indicate damper is not fully opened | The controller senses Damper Failed to OPEN. |  |  |  |  |  |  |  |
|  |  | AHU-10 Stops. |  |  |  |  |  |  |  |
|  |  | Loss of AHU Flow Reports. |  |  |  |  |  |  |  |
|  |  | The gas valve closes as a safety. |  |  |  |  |  |  |  |
|  |  | The Boiler begins shut down cycle. |  |  |  |  |  |  |  |
|  |  | The Boiler system control alarms. |  |  |  |  |  |  |  |
|  |  | A general alarm reports at BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Restore the end switch | The boiler begins startup sequence. |  |  |  |  |  |  |  |
|  |  | The boiler is ON. |  |  |  |  |  |  |  |
|  |  | The local alarm clears. |  |  |  |  |  |  |  |
|  |  | The general alarm at the BAS clears. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the boiler if not recycling be itself | The boiler begins startup sequence. |  |  |  |  |  |  |  |
|  |  | The boiler is ON. |  |  |  |  |  |  |  |
|  |  | The local alarm clears. |  |  |  |  |  |  |  |
|  |  | The general alarm at the BAS clears. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Manipulate the AHU-10 differential pressure proof-of-flow switch to indicate fan is OFF | The controller senses loss of AHU-10 FLOW. |  |  |  |  |  |  |  |
|  |  | The gas valve closes as a safety. |  |  |  |  |  |  |  |
|  |  | The Boiler begins shut down cycle. |  |  |  |  |  |  |  |
|  |  | The local control alarms. |  |  |  |  |  |  |  |
|  |  | A general alarm registers at the BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Restore the flow switch | The boiler begins startup sequence. |  |  |  |  |  |  |  |
|  |  | The boiler is ON. |  |  |  |  |  |  |  |
|  |  | The local alarm clears. |  |  |  |  |  |  |  |
|  |  | The general alarm at the BAS clears. |  |  |  |  |  |  |  |
|  |  | The boiler system operates normally. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the boiler if not recycling be itself | The boiler begins startup sequence. |  |  |  |  |  |  |  |
|  |  | The boiler is ON. |  |  |  |  |  |  |  |
|  |  | The local alarm clears. |  |  |  |  |  |  |  |
|  |  | The general alarm at the BAS clears. |  |  |  |  |  |  |  |
|  |  | The boiler system operates normally. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| ##### CONDENSATE PUMP OPERATION |  |  |  |  |  |  |  |  |  |
|  | Briefly bump each pump ON with HOA | Momentary start proves HOA ON works but does not drain too much condensate. |  |  | Use “Hand Off Auto” to turn pumps OFF in the following steps ____ Height of condensate above finished floor when Lead pump starts. |  |  |  |  |
|  |  | Lead condensate pump starts. |  |  |  |  |  |  |  |
|  |  | Record level pump starts. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | At condensate receiver tank, allow level to rise until pump starts. | Momentary start proves HOA ON works but does not drain too much condensate. |  |  | Use “Hand Off Auto” to turn pumps OFF in the following steps ____ Height of condensate above finished floor when Lead pump starts. |  |  |  |  |
|  |  | Lead condensate pump starts. |  |  |  |  |  |  |  |
|  |  | Record level pump starts. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Pump only 5 seconds then execute next step. | Momentary start proves HOA ON works but does not drain too much condensate. |  |  | Use “Hand Off Auto” to turn pumps OFF in the following steps ____ Height of condensate above finished floor when Lead pump starts. |  |  |  |  |
|  |  | Lead condensate pump starts. |  |  |  |  |  |  |  |
|  |  | Record level pump starts. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Disconnect power to or turn off the Lead condensate pump. | Lead condensate pump stops. |  |  | Note if any alarms:___________ |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Allow condensate level to rise until lag condensate pump starts | Back-up condensate pump starts. |  |  | ____” Height of condensate above finished floor when Lead pump starts. |  |  |  |  |
|  |  | Record level pump starts. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Pump only 5 seconds then execute next step. | Back-up condensate pump starts. |  |  | ____” Height of condensate above finished floor when Lead pump starts. |  |  |  |  |
|  |  | Record level pump starts. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Disconnect power to or turn off the Lag condensate pump. | Lag condensate pump stops. |  |  | Alarm Message should be clear what has failed. The piping and drain should be arranged to limit hot condensate from causing injury. |  |  |  |  |
|  |  | Alarm Reports to BAS. |  |  |  |  |  |  |  |
|  |  | There is a drain for condensate to overflow tank. |  |  |  |  |  |  |  |
|  |  | Watch boiler feed water tank for low level if it goes low and calls for water note this at end of test section G. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Wait if needed for Highest level to report Condensate pump failure alarm | Lag condensate pump stops. |  |  | Alarm Message should be clear what has failed. The piping and drain should be arranged to limit hot condensate from causing injury. |  |  |  |  |
|  |  | Alarm Reports to BAS. |  |  |  |  |  |  |  |
|  |  | There is a drain for condensate to overflow tank. |  |  |  |  |  |  |  |
|  |  | Watch boiler feed water tank for low level if it goes low and calls for water note this at end of test section G. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Restore power to or turn on the Lead then Lag condensate pump | Lead pump starts. |  |  |  |  |  |  |  |
|  |  | As level drops Alarm clears. |  |  |  |  |  |  |  |
|  |  | Condensate flows freely and without leakage to boiler system receiver tank. |  |  |  |  |  |  |  |
|  |  | When tank gets to low level the lead pump stops and switches to old lag pump. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Allow pump to run to its automatic shut off point. | Lead pump starts. |  |  |  |  |  |  |  |
|  |  | As level drops Alarm clears. |  |  |  |  |  |  |  |
|  |  | Condensate flows freely and without leakage to boiler system receiver tank. |  |  |  |  |  |  |  |
|  |  | When tank gets to low level the lead pump stops and switches to old lag pump. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Allow condensate to fill to start level | Lead pump has alternated to the old Lag pump. |  |  |  |  |  |  |  |
|  |  | New Lead pump starts. |  |  |  |  |  |  |  |
|  |  | Condensate flows freely and without leakage to boiler system receiver tank. |  |  |  |  |  |  |  |
|  |  | When tank gets to low level the lead pump stops and switches to old lag pump. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| ##### BOILER FEED WATER & CHEMICAL TREATMENT |  |  |  |  |  |  |  |  |  |
|  | Let Boiler 7 liquid level drop below demand level | Feed water pump 1 starts. |  |  | Feed water pumps 1, 2, 3 may have different assignments but one will be to one boiler and one as standby. |  |  |  |  |
|  |  | Feed water pump 2 and standby pump 3 remain OFF. |  |  |  |  |  |  |  |
|  |  | Water flows fast enough to replace boiler water before low limit safety shuts off boiler. |  |  |  |  |  |  |  |
|  |  | When water level goes high pump stops. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Let Boiler 8 liquid level drop below demand level | Feed water pump 2 starts. |  |  |  |  |  |  |  |
|  |  | Feed water pump 1 and standby pump 3 remain OFF. |  |  |  |  |  |  |  |
|  |  | Water flows fast enough to replace boiler water before low limit safety shuts off boiler. |  |  |  |  |  |  |  |
|  |  | When water level goes high pump stops. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Transfer Assignment for Boiler 7 to the standby pump. | Feed water pump 3 starts. |  |  |  |  |  |  |  |
|  |  | Feed water pump 1 and 2 remain OFF. |  |  |  |  |  |  |  |
|  |  | Water flows fast enough to replace boiler water before low limit safety shuts off boiler. |  |  |  |  |  |  |  |
|  |  | When water level rises pump stops. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Allow Boiler 7 level to rise above switch level | Feed water pump 3 starts. |  |  |  |  |  |  |  |
|  |  | Feed water pump 1 and 2 remain OFF. |  |  |  |  |  |  |  |
|  |  | Water flows fast enough to replace boiler water before low limit safety shuts off boiler. |  |  |  |  |  |  |  |
|  |  | When water level rises pump stops. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Adjust the conductivity set pt on controller to 1000 μS/cm less than the current system conductivity level or set scheduled blow down for 2 minutes. | The blow down valve is opened and the system is discharging to maintain the required conductivity level or timed release. |  |  | Submittals were not clear on what initiates blow down. Record Conductivity setting ____ Record Schedule _______ |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the conductivity set point or timer to the original value. | The converter blow down valve is closed to maintain the new conductivity requirements. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Allow or drain Feed water tank to below make up level | The cold water valve opens to add water through HX-7 into the feed water tank. |  |  |  |  |  |  |  |
|  |  | Observe reaction in test section H HX-7. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Allow Feed water tank to rise | The cold water valve Closes. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| ##### HEAT EXCHANGER HX-7 MAKE UP WATER HEATER |  |  |  |  |  |  |  |  |  |
|  | With make up water OFF the heating control valve is closed | Even with low temperature in make up water line there is no heating with make up water OFF. |  |  | If a call for make up is not observed during normal operation create a call by draining the feed water tank. Record level when make up opens______ |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Supply water temperature drops without circulation | Even with low temperature in make up water line there is no heating with make up water OFF. |  |  | If a call for make up is not observed during normal operation create a call by draining the feed water tank. Record level when make up opens______ |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Call for make up water so HX7 control is ON | Steam control valve modulates to maintain supply water temperature. |  |  | With only a short time for make up water flow the supply water may go from several degrees below set point to several above and not stabilize before make up tank is filled. |  |  |  |  |
|  |  | As temperature increases above set point valve modulates closed. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Supply water temp drops with flow | Steam control valve modulates to maintain supply water temperature. |  |  | With only a short time for make up water flow the supply water may go from several degrees below set point to several above and not stabilize before make up tank is filled. |  |  |  |  |
|  |  | As temperature increases above set point valve modulates closed. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Lower High temperature alarm set point below existing supply Temp | Local high temp limit alarm sounds. |  |  | Record high limit setpoint _____ |  |  |  |  |
|  |  | Cold water solenoid valve opens. |  |  |  |  |  |  |  |
|  |  | Over heated water is dumped from shell. |  |  |  |  |  |  |  |
|  |  | BAS Alarm reports. |  |  |  |  |  |  |  |
|  |  | Steam Valve closes. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Clear High temperature alarm | Alarm clears. |  |  |  |  |  |  |  |
|  |  | HX-7 returns to normal operation. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset alarm setpoint | Alarm clears. |  |  |  |  |  |  |  |
|  |  | HX-7 returns to normal operation. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Simulate power loss | Steam valve closes in 10 seconds. |  |  |  |  |  |  |  |
|  |  | Controller is OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Restore power | Controller returns to normal operation. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Feed water tank ends call for make up water | When cold water valve closes heating valve closes. |  |  | Record level when make up closes______ |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Restore to normal any special action required to initiate operation | System is running normally. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| ##### RETURN TO INITIAL CONDITIONS |  |  |  |  |  |  |  |  |  |
|  | Record test stop time | Recorded. |  |  | Time: (am/pm)__________ |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |

| ## Final Sign-Off |  |  |  |  |
| --- | --- | --- | --- | --- |
| Commissioning Agent | Printed Name | Initials | Date |  |
| CONTRACTOR | PRINTED NAME | INITIALS | DATE |  |
| General Contractor (GC) |  |  |  |  |
| Mechanical Contractor (MC) |  |  |  |  |
| Electrical Contractor (EC) |  |  |  |  |
| TAB Contractor (TAB) |  |  |  |  |
| Controls Contractor (CC) |  |  |  |  |
| Owner’s O&M Personnel |  |  |  |  |