# Centrifugal Water Chiller

# Functional Performance Test

| Equipment ID | [Equipment ID] |
| --- | --- |
| Building | [Building] |
| Location | [Room] |

## System Description

Description:

Operational Assumptions: Associated air handling equipment and ducts has been tested and is operating correctly. The test begins while the room is in the occupied mode.

| Initial Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 1 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 2 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Deferred/Seasonal Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

## Test Participants

| Organization | Required | Optional |
| --- | --- | --- |
| General Contractor |  |  |
| Mechanical Contractor |  |  |
| Electrical Contractor |  |  |
| TAB Contractor |  |  |
| Controls Contractor |  |  |
| Owner’s O&M Personnel |  |  |

## Supplies Required for Testing (To be provided by the contractor)

| Tools / Supplies |  |
| --- | --- |
| Laptop with TC Program | Infrared Thermometer Gun |
| PID Loop Tuning Software | Humidity Tester |
| Aerosol for Smoke and Freeze stat Test | Basic Tool Pouch |
| Radio Communications | Flashlight |

## System Readiness Summary Checklist

| Description | Yes | No | Date |
| --- | --- | --- | --- |
| System Ready for Test |  |  |  |
| Required Personnel Available |  |  |  |
| Required Tools/Test Equipment/Supplies Available |  |  |  |
| Required Safety Equipment Available |  |  |  |

## Set-Points, Limits, and Schedules

AHU can be assigned a schedule.	 Schedule can be programmed daily.

If system runs 24 hours a day, check here. If not, fill in the occupied mode schedule below.

|  | AM |  |  |  |  |  |  |  |  |  |  |  | PM |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Day | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |
| Sun |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Mon |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tues |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Wed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Thurs |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fri |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sat |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Holi |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Parameter | Setpoint |  | Adjustable Range |  |
| --- | --- | --- | --- | --- |
|  | Design | Actual | Design | Actual |
| Outside Air Temperature (°F) |  |  |  |  |
| Preheat valve full open outside air temperature (°F) |  |  |  |  |
| Discharge Air Temperature (°F) |  |  |  |  |
| Night Setback Temperature (°F) |  |  |  |  |
| Night Setback Differential |  |  |  |  |
| Mixed Air Temperature (°F) |  |  |  |  |
| Minimum Start-up Fan Speed (%) |  |  |  |  |
| Time at Minimum Fan Speed for Start-up (min) |  |  |  |  |
| Average Zone Humidity (%RH) |  |  |  |  |
| Maximum supply air humidity (%RH) |  |  |  |  |
| Discharge Air Static Pressure (in H2O) |  |  |  |  |
| High Static Alarm (in H2O) |  |  |  |  |
| Low Static Alarm (in H2O) |  |  |  |  |
| System Shutdown High Static Limit (in H2O) |  |  |  |  |
| Damper Position |  |  |  |  |

## Initial Ambient Conditions

| Ambient Conditions |  |  |  |
| --- | --- | --- | --- |
| Outside Air Temp |  | Outside Air RH % |  |
| Observations |  |  |  |

## Trend Data Required To Support Testing

Check if trend point chart(s) and Frequency Graph(s) are provided per trend requirements shown below.

| Trend Log Setup #1 - Temperature |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Pre-Testing | Post Testing | Point | Frequency | Duration | Provided |
|  |  | System Flow Rate |  |  | Yes No |
|  |  | Flow Rate Set Point |  |  | Yes No |
|  |  | Water Quality |  |  | Yes No |
|  |  | Damper Position |  |  | Yes No |
|  |  | System Pressure |  |  | Yes No |
|  |  | Pressure Set Point |  |  | Yes No |
| Record Issues |  |  |  | Issue Log Item Number: |  |

## Functional Performance Test -- (Verify all components are ready before energizing or operating the system.)

The Commissioning Authority will make and document any changes/addition/deletions to this test procedure required by current system conditions (i.e. weather, system load, utility availability, etc.).

R = Retest (Check () retest required)								Y= Checked and Passed

C = Corrected (Check () when correction verified)					              N = Not Passed

| ACTION |  | REQUIRED REACTION | Y () | N () | COMMENTS |  | R () |  | C () |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PRE-TEST VISUAL MECHANICAL INSPECTION |  |  |  |  |  |  |  |  |  |
|  | Record the starting conditions | Recorded. |  |  | Lead Chiller CH-______ Lead Chiller Status_____ Lag Chiller CH- ______ Lag Chiller Status______ Primary Pump Status_______ Lead Secondary Pump P-_____ Lead Secondary Pump Status______ Stand-by Secondary Pump P-______ Stand-by Secondary Pump Status ______ Time: (am / pm) |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Confirm equipment is operating as assumed above. If not make adjustments within the Building Automation System (BAS) | Confirmed |  |  | Time: (am / pm) |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| VERIFICATION OF MANUAL CHILLER CONTROL |  |  |  |  |  |  |  |  |  |
|  | Via the CSM’s Control Mode, set the chilled water system to Manual control. | Chiller 1 is disabled. |  |  | The specifications do not describe the relationship between pump status and chiller status. Please record any differences from the Expected Results noted during test. Starting Max Chiller Stop-to-Start Cycle Timer setpoint______min New Max Chiller Stop-to-Start Cycle Timer set-point _______ min Starting Wait for Evaporator Flow Timer set-point ______ min New Wait for Evaporator Flow Timer set-point _____ min Primary Pump P-3 ON delay _____ min Primary Pump P-4 ON delay _____ min Lead Secondary pump status______ Stand-by Secondary pump status ______ |  |  |  |  |
|  |  | Chiller 2 is disabled. |  |  |  |  |  |  |  |
|  |  | Primary pump P-3 remains ON for (insert time delay). |  |  |  |  |  |  |  |
|  |  | Primary pump P-4 remains ON for (insert time delay). |  |  |  |  |  |  |  |
|  |  | The Lead secondary chilled water pump STOPS. |  |  |  |  |  |  |  |
|  |  | The Stand-by secondary chilled water pump remains OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Command both chillers CH-1 and CH-2 to OFF. | Chiller 1 is disabled. |  |  | The specifications do not describe the relationship between pump status and chiller status. Please record any differences from the Expected Results noted during test. Starting Max Chiller Stop-to-Start Cycle Timer setpoint______min New Max Chiller Stop-to-Start Cycle Timer set-point _______ min Starting Wait for Evaporator Flow Timer set-point ______ min New Wait for Evaporator Flow Timer set-point _____ min Primary Pump P-3 ON delay _____ min Primary Pump P-4 ON delay _____ min Lead Secondary pump status______ Stand-by Secondary pump status ______ |  |  |  |  |
|  |  | Chiller 2 is disabled. |  |  |  |  |  |  |  |
|  |  | Primary pump P-3 remains ON for (insert time delay). |  |  |  |  |  |  |  |
|  |  | Primary pump P-4 remains ON for (insert time delay). |  |  |  |  |  |  |  |
|  |  | The Lead secondary chilled water pump STOPS. |  |  |  |  |  |  |  |
|  |  | The Stand-by secondary chilled water pump remains OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Adjust the Max Chiller Stop-to-Start Cycle Timer to 3 minutes. | Chiller 1 is disabled. |  |  | The specifications do not describe the relationship between pump status and chiller status. Please record any differences from the Expected Results noted during test. Starting Max Chiller Stop-to-Start Cycle Timer setpoint______min New Max Chiller Stop-to-Start Cycle Timer set-point _______ min Starting Wait for Evaporator Flow Timer set-point ______ min New Wait for Evaporator Flow Timer set-point _____ min Primary Pump P-3 ON delay _____ min Primary Pump P-4 ON delay _____ min Lead Secondary pump status______ Stand-by Secondary pump status ______ |  |  |  |  |
|  |  | Chiller 2 is disabled. |  |  |  |  |  |  |  |
|  |  | Primary pump P-3 remains ON for (insert time delay). |  |  |  |  |  |  |  |
|  |  | Primary pump P-4 remains ON for (insert time delay). |  |  |  |  |  |  |  |
|  |  | The Lead secondary chilled water pump STOPS. |  |  |  |  |  |  |  |
|  |  | The Stand-by secondary chilled water pump remains OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the Wait for Evaporator Flow Timer set-point to be 2 minutes. | Chiller 1 is disabled. |  |  | The specifications do not describe the relationship between pump status and chiller status. Please record any differences from the Expected Results noted during test. Starting Max Chiller Stop-to-Start Cycle Timer setpoint______min New Max Chiller Stop-to-Start Cycle Timer set-point _______ min Starting Wait for Evaporator Flow Timer set-point ______ min New Wait for Evaporator Flow Timer set-point _____ min Primary Pump P-3 ON delay _____ min Primary Pump P-4 ON delay _____ min Lead Secondary pump status______ Stand-by Secondary pump status ______ |  |  |  |  |
|  |  | Chiller 2 is disabled. |  |  |  |  |  |  |  |
|  |  | Primary pump P-3 remains ON for (insert time delay). |  |  |  |  |  |  |  |
|  |  | Primary pump P-4 remains ON for (insert time delay). |  |  |  |  |  |  |  |
|  |  | The Lead secondary chilled water pump STOPS. |  |  |  |  |  |  |  |
|  |  | The Stand-by secondary chilled water pump remains OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Switch the Secondary pumps to Auto Lead Designation option. | Chiller 1 is disabled. |  |  | The specifications do not describe the relationship between pump status and chiller status. Please record any differences from the Expected Results noted during test. Starting Max Chiller Stop-to-Start Cycle Timer setpoint______min New Max Chiller Stop-to-Start Cycle Timer set-point _______ min Starting Wait for Evaporator Flow Timer set-point ______ min New Wait for Evaporator Flow Timer set-point _____ min Primary Pump P-3 ON delay _____ min Primary Pump P-4 ON delay _____ min Lead Secondary pump status______ Stand-by Secondary pump status ______ |  |  |  |  |
|  |  | Chiller 2 is disabled. |  |  |  |  |  |  |  |
|  |  | Primary pump P-3 remains ON for (insert time delay). |  |  |  |  |  |  |  |
|  |  | Primary pump P-4 remains ON for (insert time delay). |  |  |  |  |  |  |  |
|  |  | The Lead secondary chilled water pump STOPS. |  |  |  |  |  |  |  |
|  |  | The Stand-by secondary chilled water pump remains OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Assign the Lead chiller to CH-1 and Lag to CH-2. | Primary pump P-3 STARTS. |  |  | Runtime for P-6_______ hours Runtime for P-7 _______ hours Lead Secondary Pump P-______ |  |  |  |  |
|  |  | After the Wait for Evaporator Flow Timer expires, Chiller CH-1 STARTS. |  |  |  |  |  |  |  |
|  |  | The secondary pump with the least amount of runtime is designated Lead and STARTS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Manually command the Lead chiller to run. | Primary pump P-3 STARTS. |  |  | Runtime for P-6_______ hours Runtime for P-7 _______ hours Lead Secondary Pump P-______ |  |  |  |  |
|  |  | After the Wait for Evaporator Flow Timer expires, Chiller CH-1 STARTS. |  |  |  |  |  |  |  |
|  |  | The secondary pump with the least amount of runtime is designated Lead and STARTS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Manually command the Lag chiller to run. | Primary pump P-4 starts. |  |  |  |  |  |  |  |
|  |  | After Wait For Evaporator Flow Timer expires, Chiller CH-2 starts. |  |  |  |  |  |  |  |
|  |  | The Lead secondary chilled water pump continues to modulate. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Manually command the Lead chiller to stop. | Chiller CH-1 is de-energized. |  |  | Primary Pump P-3 ON delay _____ min |  |  |  |  |
|  |  | Primary pump P-3 remains ON for (insert time delay). |  |  |  |  |  |  |  |
|  |  | Chiller CH-2 remains ON. |  |  |  |  |  |  |  |
|  |  | Primary pump P-4 remains ON. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Manually command the Lag chiller to stop. | Chiller CH-2 is de-energized. |  |  | It is not clear whether the Lead secondary pump stops when no chillers are ON or not until the chilled water system has officially been disabled. Please record any variations witnessed in the field. Primary Pump P-4 ON delay _____ min |  |  |  |  |
|  |  | Primary pump P-4 remains ON for (insert time delay). |  |  |  |  |  |  |  |
|  |  | The Lead secondary chilled water pump STOPS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| VERIFICATION OF AUTOMATIC CHILLER CONTROL |  |  |  |  |  |  |  |  |  |
|  | Via the CSM’s Control Mode, set the chilled water system to Automatic Control. | After 2 minutes, the chilled water system is enabled. |  |  | CH-1 Runtime_________ CH-2 Runtime_________ Lead Chiller CH-_______ Primary Pump P-______ is ON. Lead Secondary Pump P-_____is ON. |  |  |  |  |
|  |  | The Lead secondary chilled water pump STARTS. |  |  |  |  |  |  |  |
|  |  | The chiller with the least amount of run-time is enabled and labeled as Lead. |  |  |  |  |  |  |  |
|  |  | The primary pump associated with the Lead chiller starts. |  |  |  |  |  |  |  |
|  |  | After the Wait for Evaporator Flow Timer, the Lead chiller is energized. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Set chiller sequencing to be according to runtime. | After 2 minutes, the chilled water system is enabled. |  |  | CH-1 Runtime_________ CH-2 Runtime_________ Lead Chiller CH-_______ Primary Pump P-______ is ON. Lead Secondary Pump P-_____is ON. |  |  |  |  |
|  |  | The Lead secondary chilled water pump STARTS. |  |  |  |  |  |  |  |
|  |  | The chiller with the least amount of run-time is enabled and labeled as Lead. |  |  |  |  |  |  |  |
|  |  | The primary pump associated with the Lead chiller starts. |  |  |  |  |  |  |  |
|  |  | After the Wait for Evaporator Flow Timer, the Lead chiller is energized. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Set the chilled water schedule to enable system in 2 minutes at the BAS. | After 2 minutes, the chilled water system is enabled. |  |  | CH-1 Runtime_________ CH-2 Runtime_________ Lead Chiller CH-_______ Primary Pump P-______ is ON. Lead Secondary Pump P-_____is ON. |  |  |  |  |
|  |  | The Lead secondary chilled water pump STARTS. |  |  |  |  |  |  |  |
|  |  | The chiller with the least amount of run-time is enabled and labeled as Lead. |  |  |  |  |  |  |  |
|  |  | The primary pump associated with the Lead chiller starts. |  |  |  |  |  |  |  |
|  |  | After the Wait for Evaporator Flow Timer, the Lead chiller is energized. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Simulate a Lead chiller failure. | Lead chiller de-energizes. |  |  |  |  |  |  |  |
|  |  | Lead chiller failure alarm generated at the CSM panel. |  |  |  |  |  |  |  |
|  |  | Lead chiller failure alarm generated at BAS. |  |  |  |  |  |  |  |
|  |  | The Lag chiller is enabled. |  |  |  |  |  |  |  |
|  |  | The primary pump for the Lead chiller STOPS. |  |  |  |  |  |  |  |
|  |  | The primary pump for the Lag chiller STARTS. |  |  |  |  |  |  |  |
|  |  | The Lag chiller is energized. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Simulate a Lag chiller failure. | Lag chiller de-energizes. |  |  |  |  |  |  |  |
|  |  | Lag chiller failure alarm generated at the CSM panel. |  |  |  |  |  |  |  |
|  |  | Lag chiller failure alarm generated at BAS. |  |  |  |  |  |  |  |
|  |  | The primary pump for the Lag chiller STOPS. |  |  |  |  |  |  |  |
|  |  | The Lead secondary pump STOPS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the Lead chiller failure condition. | The Lead secondary pump STARTS. |  |  | Lead chiller CH-_____ Lead Secondary Pump P-______ |  |  |  |  |
|  |  | The Lead chiller is enabled. |  |  |  |  |  |  |  |
|  |  | The primary pump for the Lead chiller STARTS. |  |  |  |  |  |  |  |
|  |  | After the Wait for Evaporator Flow Timer expires, the Lead chiller energizes. |  |  |  |  |  |  |  |
|  |  | Chiller failure alarm clears at BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Manually reset the Lead chiller failure alarm at the CSM panel. | The Lead secondary pump STARTS. |  |  | Lead chiller CH-_____ Lead Secondary Pump P-______ |  |  |  |  |
|  |  | The Lead chiller is enabled. |  |  |  |  |  |  |  |
|  |  | The primary pump for the Lead chiller STARTS. |  |  |  |  |  |  |  |
|  |  | After the Wait for Evaporator Flow Timer expires, the Lead chiller energizes. |  |  |  |  |  |  |  |
|  |  | Chiller failure alarm clears at BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the Lag chiller failure condition. | Chiller failure alarm clears at BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Manually reset the Lag chiller failure alarm at the CSM panel. | Chiller failure alarm clears at BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Set the chiller sequencing time of day schedule to disable chilled water system in 2 minutes at the BAS. | After 2 minutes, the Lead chiller de-energizes and is disabled. |  |  |  |  |  |  |  |
|  |  | After a delay, the primary pump for the Lead chiller stops. |  |  |  |  |  |  |  |
|  |  | The Lead secondary pump STOPS. |  |  |  |  |  |  |  |
|  |  | The Lag chiller and its primary pump remain OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Switch the Secondary Lead Pump Designation back to its original selection criteria (Manual/Auto) |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| VERIFICATION OF CHILLER CAPACITY STAGING CONTROL |  |  |  |  |  |  |  |  |  |
|  | Designate chiller CH-2 to be the “First on” chiller through the Chiller Sequencing feature. | The chilled water system is enabled. |  |  | Steps 24-?? assume that the (Decoupler Line Temperature) < (Chilled Water Supply Temperature + Decoupler Stage-Up Temperature Differential) Lead Secondary Pump P-_____ |  |  |  |  |
|  |  | The Lead secondary pump STARTS. |  |  |  |  |  |  |  |
|  |  | Chiller CH-2 is enabled. |  |  |  |  |  |  |  |
|  |  | Primary pump P-4 starts. |  |  |  |  |  |  |  |
|  |  | After the Wait for Evaporator Flow Timer, Chiller CH-2 is energized. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Via the “Operator Scheduled Override” option, enable the chilled water system. | The chilled water system is enabled. |  |  | Steps 24-?? assume that the (Decoupler Line Temperature) < (Chilled Water Supply Temperature + Decoupler Stage-Up Temperature Differential) Lead Secondary Pump P-_____ |  |  |  |  |
|  |  | The Lead secondary pump STARTS. |  |  |  |  |  |  |  |
|  |  | Chiller CH-2 is enabled. |  |  |  |  |  |  |  |
|  |  | Primary pump P-4 starts. |  |  |  |  |  |  |  |
|  |  | After the Wait for Evaporator Flow Timer, Chiller CH-2 is energized. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the Chiller Stage-up Differential to be 30F. | Primary pump P-4 is ON. |  |  | Starting Chilled Water Supply Temperature set-point ______ F Ending Chilled Water Supply Temperature set-point ______ F |  |  |  |  |
|  |  | CH-2 is at full load. |  |  |  |  |  |  |  |
|  |  | CH-1 remains OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the Chiller Stage Delay Time variable to be 60 minutes. | Primary pump P-4 is ON. |  |  | Starting Chilled Water Supply Temperature set-point ______ F Ending Chilled Water Supply Temperature set-point ______ F |  |  |  |  |
|  |  | CH-2 is at full load. |  |  |  |  |  |  |  |
|  |  | CH-1 remains OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Decrease the Chilled Water Supply Temperature set-point in 1F increments below the current chilled water supply temperature until Lead chiller is at full load. | Primary pump P-4 is ON. |  |  | Starting Chilled Water Supply Temperature set-point ______ F Ending Chilled Water Supply Temperature set-point ______ F |  |  |  |  |
|  |  | Primary pump P-4 is ON. |  |  |  |  |  |  |  |
|  |  | CH-1 remains OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Adjust the Chiller Stage-up Differential to be 2F. | Chiller CH-2 remains at full load. |  |  |  |  |  |  |  |
|  |  | Lag chiller CH-1 remains OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Adjust the Chilled Water Supply Temperature set-point to be 5F below the current chilled water supply temperature. | Chiller CH-2 remains at full load. |  |  |  |  |  |  |  |
|  |  | Lag chiller CH-1 remains OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the Chiller Stage Delay Time variable to be 2 minutes. | After 2 minutes, the Lag chiller CH. |  |  | New Chilled Water Supply Temperature set-point ______ F |  |  |  |  |
|  |  | Primary pump P. |  |  |  |  |  |  |  |
|  |  | After the Wait for Evaporator Flow Timer expires, CH. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the Chiller Stage Delay Time variable to be 60 minutes. | Chillers CH-1 and CH-2 remain ON. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Adjust the Active Capacity set-point to be less than (Spare Capacity Factor * Sum of All Spare Capacity of All Running Chillers). | Chillers CH-1 and CH-2 remain ON. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the Chiller Stage Delay Time variable to be 2 minutes. | After 2 minutes, Chiller CH. |  |  | New Active Capacity set-point _____ |  |  |  |  |
|  |  | After a time delay, primary pump P. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| VERIFICATION OF CHILLER FLOW STAGING CONTROL |  |  |  |  |  |  |  |  |  |
|  | Adjust the Chilled Water Supply Temperature set-point to be 1F above the current chilled water supply temperature. | CH-2 is not at full load. |  |  |  |  |  |  |  |
|  |  | CH-1 remains OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the Chiller Stage Delay Time variable to be 60 minutes. | CH-2 is not at full load. |  |  |  |  |  |  |  |
|  |  | CH-1 remains OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Adjust the Decoupler Stage-Up Temperature Differential Set-Point so the following is true: (Current Decoupler Line Temperature + Decoupler Stage-Up Temperature Differential Set-Point) > Current chilled water supply temperature | CH-2 is not at full load. |  |  |  |  |  |  |  |
|  |  | CH-1 remains OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the Chiller Stage Delay Time variable to be 2 minutes. | After 2 minutes, the Lag chiller CH. |  |  |  |  |  |  |  |
|  |  | Primary pump P. |  |  |  |  |  |  |  |
|  |  | After the Wait for Evaporator Flow Timer expires, chiller CH. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Override the Active Capacity input on CH-1 to be less than (Spare Capacity Factor*Sum of All Spare Capacity of All Remaining Chillers) | After 2 minutes, the Lag chiller remains ON. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Adjust the Chiller Stage Delay Time variable to be 60 minutes. | Both the Lead and Lag chillers remain ON. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Adjust the Decoupler Stage-Down Flow Rate Factor set-point to be greater than (the Current Decoupler Flow Rate/Current Lag Chiller Flow Rate). | Both the Lead and Lag chillers remain ON. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Adjust the Chiller Stage Delay Time variable to be 2 minutes. | After 2 minutes, the Lag Chiller CH. |  |  |  |  |  |  |  |
|  |  | After a time delay, primary pump P. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Return the Chiller Stage Delay Time variable to its original value. | System resumes normal operation. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Return the Decoupler Stage-Down Flow Rate Factor set-point back to its original value. | System resumes normal operation. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Release the Active Capacity input override for CH-1. | System resumes normal operation. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Return the Decoupler Stage-Up Temperature Differential set-point back to its original value. | System resumes normal operation. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Return the chilled water supply temperature set-point back to its original value. | System resumes normal operation. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Return the Chiller Stage-Up Differential Temperature set-point back to its original value. | System resumes normal operation. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Return the Chiller Sequencing option back to original selection. | System resumes normal operation. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| VERIFICATION OF AUTOMATIC PUMP SPEED CONTROL |  |  |  |  |  |  |  |  |  |
|  | Decrease the differential pressure set-point by 20%. | The Lead secondary chilled water pump speed decreases. |  |  | It is the understanding of the test writer that there are two secondary pumps each sized at 100% of the load. The test is written around a Lead/Stand-by configuration. If in the field it is determined that this is not the correct operation, the test steps will need to be field modified . Starting Differential Pressure setpoint______psi Adjusted Differential Pressure Setpoint:_______psi |  |  |  |  |
|  |  | The Stand-by secondary chilled water pump is OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Increase the differential pressure set-point by 20%. | The Lead secondary chilled water pump speed increases. |  |  | New Differential Pressure Set-Point:_____ |  |  |  |  |
|  |  | The Stand-by pump remains OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Manually reassign secondary pump designations, Lead and Stand-by. | No changes are noted. The old Lead pump remains ON. The old Stand-by pump remains OFF. |  |  | The sequence states the only under certain conditions will the system implement the new Lead pump if the chilled water system is already enabled. This step is to show that this is not one of those conditions. |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Switch the pumps back to their original designation. | No changes are noted. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the Pump Status Check Delay Time variable to 30 seconds. | The Lead secondary pump stops |  |  |  |  |  |  |  |
|  |  | After 30 seconds, the Stand-by secondary pump starts. |  |  |  |  |  |  |  |
|  |  | A Pump Failure alarm sounds at the CSM panel. |  |  |  |  |  |  |  |
|  |  | A Pump Failure alarm sounds at the BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Simulate a loss of power pump failure at the Lead secondary chilled water pump. | The Lead secondary pump stops. |  |  |  |  |  |  |  |
|  |  | After 30 seconds, the Stand-by secondary pump starts. |  |  |  |  |  |  |  |
|  |  | A Pump Failure alarm sounds at the CSM panel. |  |  |  |  |  |  |  |
|  |  | A Pump Failure alarm sounds at the BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Decrease the differential pressure set-point by 20% | The Stand-by secondary chilled water pump speed decreases. |  |  | New Differential Pressure set-point ______ psi. |  |  |  |  |
|  |  | The Lead secondary chilled water pump remains OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Increase the differential pressure set-point by 20% | The Stand-by secondary chilled water pump speed increases. |  |  | New Differential Pressure set-point ______ psi. |  |  |  |  |
|  |  | The Lead secondary chilled water pump remains OFF. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Simulate a loss of power pump failure at the Stand-by secondary chilled water pump. | The Stand-by secondary pump STOPS. |  |  | Intent is to show that in cases with failure of both secondary chilled water pumps, the entire chilled water system is disabled. |  |  |  |  |
|  |  | The Lead secondary pump is OFF. |  |  |  |  |  |  |  |
|  |  | A “No Chilled Water Flow” alarm sounds at the CSM panel. |  |  |  |  |  |  |  |
|  |  | A Pump Failure alarm sounds at the BAS. |  |  |  |  |  |  |  |
|  |  | Both chillers de-energize. |  |  |  |  |  |  |  |
|  |  | The primary pumps STOP. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Restore power to the Stand-by secondary chilled water pump. | The system remains disabled. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Manually reset Standby Pump Failure alarm at the CSM panel. | The Stand-by Pump Failure alarm is cleared at the BAS. |  |  |  |  |  |  |  |
|  |  | The chilled water system is enabled. |  |  |  |  |  |  |  |
|  |  | The Stand-by secondary pump STARTS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Restore power to the Lead secondary chilled water pump. | The Lead secondary chilled water pump STARTS. |  |  | The sequence is unclear if this is a condition where the previously stopped Lead pump would be brought back into service automatically. Please note variations seen in the field. |  |  |  |  |
|  |  | The Stand-by secondary chilled water pump STOPS. |  |  |  |  |  |  |  |
|  |  | The Pump Failure alarm clears at the BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Manually reset the Lead Pump Failure alarm at the CSM panel. | The Lead secondary chilled water pump STARTS. |  |  | The sequence is unclear if this is a condition where the previously stopped Lead pump would be brought back into service automatically. Please note variations seen in the field. |  |  |  |  |
|  |  | The Stand-by secondary chilled water pump STOPS. |  |  |  |  |  |  |  |
|  |  | The Pump Failure alarm clears at the BAS. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Return the differential pressure set-point back to its original value. | System resumes normal operation. |  |  | Ending Differential Pressure Set-Point:_____ Ending Pump Status Check Delay Time variable ______ |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Reset the Pump Status Check Delay Time variable back to its original value. | System resumes normal operation. |  |  | Ending Differential Pressure Set-Point:_____ Ending Pump Status Check Delay Time variable ______ |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Switch Secondary Lead/Stand-by pump designation selection back to its original method (Auto/Manual) | System resumes normal operation. |  |  | Ending Differential Pressure Set-Point:_____ Ending Pump Status Check Delay Time variable ______ |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Ensure all control points are set to original values and/or conditions. | System resumes normal operation. |  |  | Ending Differential Pressure Set-Point:_____ Ending Pump Status Check Delay Time variable ______ |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| RETURN TO INITIAL CONDITIONS |  |  |  |  |  |  |  |  |  |
|  | Record test stop time | Recorded. |  |  | Time: (am / pm) |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |

| ## Final Sign-Off |  |  |  |  |
| --- | --- | --- | --- | --- |
| Commissioning Agent | Printed Name | Initials | Date |  |
| CONTRACTOR | PRINTED NAME | INITIALS | DATE |  |
| General Contractor (GC) |  |  |  |  |
| Mechanical Contractor (MC) |  |  |  |  |
| Electrical Contractor (EC) |  |  |  |  |
| TAB Contractor (TAB) |  |  |  |  |
| Controls Contractor (CC) |  |  |  |  |
| Owner’s O&M Personnel |  |  |  |  |