# Modular Indoor Central Station Air Handling Unit

# Functional Performance Test

| Equipment ID | [Equipment ID] |
| --- | --- |
| Building | [Building] |
| Location | [Room] |

## System Description

Description:

Operational Assumptions: Associated air handling equipment and ducts has been tested and is operating correctly. The test begins while the room is in the occupied mode.

| Initial Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 1 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 2 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Deferred/Seasonal Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

## Test Participants

| Organization | Required | Optional |
| --- | --- | --- |
| General Contractor |  |  |
| Mechanical Contractor |  |  |
| Electrical Contractor |  |  |
| TAB Contractor |  |  |
| Controls Contractor |  |  |
| Owner’s O&M Personnel |  |  |

## Supplies Required for Testing (To be provided by the contractor)

| Tools / Supplies |  |
| --- | --- |
| Laptop with TC Program | Infrared Thermometer Gun |
| PID Loop Tuning Software | Humidity Tester |
| Aerosol for Smoke and Freeze stat Test | Basic Tool Pouch |
| Radio Communications | Flashlight |

## System Readiness Summary Checklist

| Description | Yes | No | Date |
| --- | --- | --- | --- |
| System Readiness Checklist has been completed (SRC) |  |  |  |
| System Ready for Test |  |  |  |
| Required Personnel Available |  |  |  |
| Required Tools/Test Equipment/Supplies Available |  |  |  |
| Required Safety Equipment Available |  |  |  |

## Set-Points, Limits, and Schedules

AHU can be assigned a schedule.	 Schedule can be programmed daily.

If system runs 24 hours a day, check here. If not, fill in the occupied mode schedule below.

|  | AM |  |  |  |  |  |  |  |  |  |  |  | PM |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Day | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |
| Sun |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Mon |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tues |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Wed |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Thurs |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Fri |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sat |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Holi |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

| Parameter | Setpoint |  | Adjustable Range |  |
| --- | --- | --- | --- | --- |
|  | Design | Actual | Design | Actual |
| Outside Air Temperature (°F) |  |  |  |  |
| Preheat valve full open outside air temperature (°F) |  |  |  |  |
| Discharge Air Temperature (°F) |  |  |  |  |
| Night Setback Temperature (°F) |  |  |  |  |
| Night Setback Differential |  |  |  |  |
| Mixed Air Temperature (°F) |  |  |  |  |
| Minimum Start-up Fan Speed (%) |  |  |  |  |
| Time at Minimum Fan Speed for Start-up (min) |  |  |  |  |
| Average Zone Humidity (%RH) |  |  |  |  |
| Maximum supply air humidity (%RH) |  |  |  |  |
| Discharge Air Static Pressure (in H2O) |  |  |  |  |
| High Static Alarm (in H2O) |  |  |  |  |
| Low Static Alarm (in H2O) |  |  |  |  |
| System Shutdown High Static Limit (in H2O) |  |  |  |  |
| Damper Position |  |  |  |  |

## Initial Ambient Conditions

| Ambient Conditions |  |  |  |
| --- | --- | --- | --- |
| Outside Air Temp |  | Outside Air RH % |  |
| Precipitation |  |  |  |

## Trend Data Required To Support Testing

Check if trend point chart(s) and Frequency Graph(s) are provided per trend requirements shown below.

| Trend Log Setup #1 – Temperature |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Pre-Testing | Post Testing | Point | Frequency | Duration | Initial Value | Provided |
|  |  | Outside Air Temperature (°F) |  |  |  | Yes No |
|  |  | Preheat valve full open outside air temperature (°F) |  |  |  | Yes No |
|  |  | Discharge Air Temperature (°F) |  |  |  | Yes No |
|  |  | Night Setback Temperature (°F) |  |  |  | Yes No |
|  |  | Night Setback Differential |  |  |  | Yes No |
|  |  | Mixed Air Temperature (°F) |  |  |  | Yes No |
| Record Issues |  |  |  | Issue Log Item Number: |  |  |

Check if trend point chart(s) and Frequency Graph(s) are provided per trend requirements shown below.

| Trend Log Setup #2 – Global |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Pre-Testing | Post Testing | Point | Frequency | Duration | Initial Value | Provided |
|  |  | System Flow Rate |  |  |  | Yes No |
|  |  | Flow Rate Set Point |  |  |  | Yes No |
|  |  | Water Quality |  |  |  | Yes No |
|  |  | Damper Position |  |  |  | Yes No |
|  |  | System Pressure |  |  |  | Yes No |
|  |  | Pressure Set Point |  |  |  | Yes No |
| Record Issues |  |  |  | Issue Log Item Number: |  |  |

## Functional Performance Test -- (Verify all components are ready before energizing or operating the system.)

The Commissioning Authority will make and document any changes/addition/deletions to this test procedure required by current system conditions (i.e. weather, system load, utility availability, etc.).

R = Retest (Check () retest required)								Y= Checked and Passed

C = Corrected (Check () when correction verified)					              N = Not Passed

| ACTION |  | REQUIRED REACTION | Y () | N () | COMMENTS |  |  | R () |  | C () |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PRE-TEST VISUAL PRELIMINARY DATA AND INSPECTION |  |  |  |  |  |  |  |  |  |  |
|  | Record the current values for all the required trending points in Trend Log table above. | Recorded. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Confirm equipment is operating normally as assumed above. If not make adjustments within the Building Automation System (BAS) | Confirmed. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| RETURN / EXHAUST FAN SECTION |  |  |  |  |  |  |  |  |  |  |
|  | Command the Return / Exhaust Fan to stop “OFF” | Return / Exhaust Fan is off. |  |  |  |  |  |  |  |  |
|  |  | Return / Exhaust Fan VFD commanded to 0%. |  |  |  |  |  |  |  |  |
|  |  | Return / Exhaust Fan Status device indicates fan is OFF. |  |  |  |  |  |  |  |  |
|  |  | Fan isolation damper closed. |  |  |  |  |  |  |  |  |
|  |  | Outside air damper is closed. |  |  |  |  |  |  |  |  |
|  |  | Return air damper is 100% open. |  |  |  |  |  |  |  |  |
|  |  | Exhaust air damper is closed. |  |  |  |  |  |  |  |  |
|  |  | Humidifier is off and commanded to 0%. |  |  |  |  |  |  |  |  |
|  |  | Face & bypass remain under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Preheat valve remains under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Cooling valve is closed. |  |  |  |  |  |  |  |  |
|  |  | R.A. quantity confirmed by airflow measuring station. |  |  | R.A. Quantity Observed ______________ CFM E.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | E.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command the Return / Exhaust Fan “ON” | Outside air damper opens. |  |  | Minimum Return / Exhaust Fan VFD minimum speed:_______ Ramp Up time to achieve minimum speed:______ |  |  |  |  |  |
|  |  | Wall mounted outside, return, and exhaust air unit mounted dampers open fully. |  |  |  |  |  |  |  |  |
|  |  | Return / Exhaust damper opens. |  |  |  |  |  |  |  |  |
|  |  | Return / Exhaust Fan VFD shall be commanded to run at minimum speed. |  |  |  |  |  |  |  |  |
|  |  | Return / Exhaust Fan Status device indicates the unit is ON while operating at a minimum speed. |  |  |  |  |  |  |  |  |
|  |  | Return / Exhaust Fan speed modulates to maintain return / exhaust differential pressure set-point. |  |  |  |  |  |  |  |  |
|  |  | Cooling valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Humidifier valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Preheat valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Face and bypass dampers is under BAS control. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| ECONOMIZER SECTION (3-DAMPER SECTION) |  |  |  |  |  |  |  |  |  |  |
|  | Minimum O.A. damper (2-position) commanded closed | Damper closes tightly without binding for complete travel distance. |  |  | O.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | Status device indicates minimum O.A. damper is closed. |  |  |  |  |  |  |  |  |
|  |  | Minimum O.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Minimum O.A. damper (2-position) commanded open | Damper opens fully without binding for complete travel distance. |  |  | O.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | Status device indicates minimum O.A. damper is open. |  |  |  |  |  |  |  |  |
|  |  | Minimum O.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | O.A. damper (modulating) commanded closed | Damper closes tightly without binding for complete travel distance. |  |  | O.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | Status device indicates O.A. damper is closed. |  |  |  |  |  |  |  |  |
|  |  | O.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | O.A. damper (modulating) commanded to 100% open | Damper opens fully without binding for complete travel distance. |  |  | O.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | Status device indicates minimum O.A. damper is open. |  |  |  |  |  |  |  |  |
|  |  | O.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | O.A. damper (modulating) commanded to 50% open | Damper opens half way without binding for complete travel distance. |  |  | O.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | Status device indicates minimum O.A. damper is open. |  |  |  |  |  |  |  |  |
|  |  | O.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | R.A. damper (modulating) commanded closed | Damper closes tightly without binding for complete travel distance. |  |  | O.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | Status device indicates R.A. damper is closed. |  |  |  |  |  |  |  |  |
|  |  | R.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | R.A. damper (modulating) commanded to 100% open | Damper opens fully without binding for complete travel distance. |  |  | O.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | Status device indicates minimum R.A. damper is open. |  |  |  |  |  |  |  |  |
|  |  | R.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | R.A. damper (modulating) commanded to 50% open | Damper opens half way without binding for complete travel distance. |  |  | O.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | Status device indicates minimum R.A. damper is open. |  |  |  |  |  |  |  |  |
|  |  | R.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | M.A. damper (modulating) commanded closed | Damper closes tightly without binding for complete travel distance. |  |  | O.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | Status device indicates M.A. damper is closed. |  |  |  |  |  |  |  |  |
|  |  | M.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | M.A. damper (modulating) commanded to 100% open | Damper opens fully without binding for complete travel distance. |  |  | O.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | Status device indicates minimum M.A. damper is open. |  |  |  |  |  |  |  |  |
|  |  | M.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | M.A. damper (modulating) commanded to 50% open | Damper opens half way without binding for complete travel distance. |  |  | O.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | Status device indicates minimum M.A. damper is open. |  |  |  |  |  |  |  |  |
|  |  | M.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Release all damper overrides. | Dampers return to normal operating positions. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| MIXING BOX SECTION (2-DAMPER SECTION) |  |  |  |  |  |  |  |  |  |  |
|  | O.A. damper commanded fully closed | Damper closes tightly without binding for complete travel distance. |  |  | O.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | Status device indicates O.A. damper is closed. |  |  |  |  |  |  |  |  |
|  |  | O.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial |  | Date |  |  |  |
|  | O.A. damper commanded fully open | Damper opens fully without binding for complete travel distance. |  |  | O.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | Status device indicates minimum O.A. damper is open. |  |  |  |  |  |  |  |  |
|  |  | O.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial |  | Date |  |  |  |
|  | O.A. damper commanded 50% open | Damper opens fully without binding for complete travel distance. |  |  | O.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | Status device indicates minimum O.A. damper is open. |  |  |  |  |  |  |  |  |
|  |  | O.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial |  | Date |  |  |  |
|  | R.A. damper commanded fully closed | Damper closes tightly without binding for complete travel distance. |  |  | R.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | Status device indicates R.A. damper is closed. |  |  |  |  |  |  |  |  |
|  |  | R.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record Issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial |  | Date |  |  |  |
|  | R.A. damper commanded fully open | Damper opens fully without binding for complete travel distance. |  |  | R.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | Status device indicates minimum O.A. damper is open. |  |  |  |  |  |  |  |  |
|  |  | O.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial |  | Date |  |  |  |
|  | R.A. damper commanded 50% open | Damper opens fully without binding for complete travel distance. |  |  | R.A. Quantity Observed ______________ CFM |  |  |  |  |  |
|  |  | Status device indicates minimum O.A. damper is open. |  |  |  |  |  |  |  |  |
|  |  | O.A. quantity confirmed by airflow measuring station. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial |  | Date |  |  |  |
|  | Release all damper overrides. | Dampers return to normal operating positions. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| PRE-FILTER SECTION |  |  |  |  |  |  |  |  |  |  |
|  | Activate the filter high pressure differential switch by applying pressure to the high side of the switch. | Dirty filter alarm indicated at BAS. |  |  | Filter Pressure at alarm _____________ in. WC |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial |  | Date |  |  |  |
|  | Release pressure from high side of switch and return to its normal condition. | Dirty filter alarm cleared at BAS. |  |  | Filter Pressure at alarm _____________ in. WC |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial |  | Date |  |  |  |
| ENTHALPY WHEEL |  |  |  |  |  |  |  |  |  |  |
|  | Command enthalpy wheel to stop. | Enthalpy wheel rotation stops. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command enthalpy wheel rotate at its maximum speed. | Enthalpy wheel rotation begins, and in the correct direction. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command enthalpy wheel rotate at 50% of its maximum speed. | Enthalpy wheel rotation slows to 50% of its maximum speed. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| FACE AND BYPASS DAMPERS |  |  |  |  |  |  |  |  |  |  |
|  | Face and bypass dampers commanded fully open. | Face damper opens fully without binding for complete travel distance. |  |  |  |  |  |  |  |  |
|  |  | Status device indicates face damper is fully open. |  |  |  |  |  |  |  |  |
|  |  | Bypass damper opens fully without binding for complete travel distance. |  |  |  |  |  |  |  |  |
|  |  | Status device indicates bypass damper is fully open. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Face damper commanded to fully closed | Damper closes tightly without binding for complete travel distance. |  |  |  |  |  |  |  |  |
|  |  | Status device indicates face damper is closed. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Face damper commanded to 50% open | Damper opens half way without binding for complete travel distance. |  |  |  |  |  |  |  |  |
|  |  | Status device indicates damper is open. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Face damper commanded fully open. Bypass damper commanded fully closed. | Face damper opens fully. |  |  |  |  |  |  |  |  |
|  |  | Status device indicates face damper is fully open. |  |  |  |  |  |  |  |  |
|  |  | Bypass damper opens fully without binding for complete travel distance. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Bypass damper commanded to 50% open | Damper opens half way without binding for complete travel distance. |  |  |  |  |  |  |  |  |
|  |  | Status device indicates damper is open. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Release all damper overrides. | Dampers return to normal operating positions. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| DRAW-THRU COIL SECTION |  |  |  |  |  |  |  |  |  |  |
|  | Command preheat coil control valve to 100% open. | Preheat coil valve fully opens. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command preheat coil control valve to close fully. | Preheat coil valve fully closes. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command preheat coil control valve to 50% open. | Preheat coil control valve opens to 50%. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Remove power from the preheat control valve actuator. | Preheat coil control valve moves to its fail safe position (fully open). |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Release overrides on preheat coil valve. | Preheat coil control valve returns to normal operation. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command chilled water coil control valve to 100% open. | Chilled water coil valve fully opens. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command chilled water coil control valve to close fully. | Chilled water coil valve fully closes. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command chilled water coil control valve to 50% open. | Chilled water coil control valve opens to 50%. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Remove power from the chilled water control valve actuator. | Chilled water coil control valve moves to its fail safe position (fully closed). |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Release override on chilled water coil valve. | Chilled water coil control valve returns to normal operation. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Coil Pump |  |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| HORIZONTAL COIL SECTION |  |  |  |  |  |  |  |  |  |  |
|  | Command preheat coil control valve to 100% open. | Preheat coil valve fully opens. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command preheat coil control valve to close fully. | Preheat coil valve fully closes. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command preheat coil control valve to 50% open. | Preheat coil control valve opens to 50%. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Remove power from the preheat control valve actuator. | Preheat coil control valve moves to its fail safe position (fully open). |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Release overrides on preheat coil valve. | Preheat coil control valve returns to normal operation. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command chilled water coil control valve to 100% open. | Chilled water coil valve fully opens. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command chilled water coil control valve to close fully. | Chilled water coil valve fully closes. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command chilled water coil control valve to 50% open. | Chilled water coil control valve opens to 50%. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Remove power from the chilled water control valve actuator. | Chilled water coil control valve moves to its fail safe position (fully closed). |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Release override on chilled water coil valve. | Chilled water coil control valve returns to normal operation. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Coil Pump |  |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| SUPPLY FAN SECTION |  |  |  |  |  |  |  |  |  |  |
|  | Command the Supply Fan to stop “OFF” | Supply Fan is off. |  |  |  |  |  |  |  |  |
|  |  | Supply Fan VFD commanded to 0%. |  |  |  |  |  |  |  |  |
|  |  | Supply Fan Status device indicates fan is OFF. |  |  |  |  |  |  |  |  |
|  |  | Fan isolation damper closed. |  |  |  |  |  |  |  |  |
|  |  | Outside air damper is closed. |  |  |  |  |  |  |  |  |
|  |  | Return air damper is 100% open. |  |  |  |  |  |  |  |  |
|  |  | Exhaust air damper is closed. |  |  |  |  |  |  |  |  |
|  |  | Humidifier is off and commanded to 0%. |  |  |  |  |  |  |  |  |
|  |  | Face & bypass remain under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Preheat valve remains under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Cooling valve is closed. |  |  |  |  |  |  |  |  |
|  |  | S.A. quantity confirmed by airflow measuring station. |  |  | S.A. Quantity Observed ______________ CFM |  |  |  |  |  |
| Record issue |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command the Supply Fan “ON” | Outside air damper opens. |  |  | Minimum Return / Exhaust Fan VFD minimum speed:_______ Ramp Up time to achieve minimum speed:______ |  |  |  |  |  |
|  |  | Wall mounted outside, return, and exhaust air unit mounted dampers open fully. |  |  |  |  |  |  |  |  |
|  |  | Supply damper opens. |  |  |  |  |  |  |  |  |
|  |  | Supply Fan VFD shall be commanded to run at minimum speed. |  |  |  |  |  |  |  |  |
|  |  | Supply Fan Status device indicates the unit is ON while operating at a minimum speed. |  |  |  |  |  |  |  |  |
|  |  | Supply Fan speed modulates to maintain supply duct pressure set-point. |  |  |  |  |  |  |  |  |
|  |  | Cooling valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Humidifier valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Preheat valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Face and bypass dampers is under BAS control. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| BLOW-THRU COIL SECTION |  |  |  |  |  |  |  |  |  |  |
|  | Command reheat coil control valve to 100% open. | Reheat coil valve fully opens. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command reheat coil control valve to close fully. | Reheat coil valve fully closes. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command reheat coil control valve to 50% open. | Reheat coil control valve opens to 50%. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Remove power from the reheat control valve actuator. | Reheat coil control valve moves to its fail safe position (fully open). |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Release overrides on reheat coil valve. | Preheat coil control valve returns to normal operation. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command chilled water coil control valve to 100% open. | Chilled water coil valve fully opens. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command chilled water coil control valve to close fully. | Chilled water coil valve fully closes. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command chilled water coil control valve to 50% open. | Chilled water coil control valve opens to 50%. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Remove power from the chilled water control valve actuator. | Chilled water coil control valve moves to its fail safe position (fully closed). |  |  | . |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Release override on chilled water coil valve. | Chilled water coil control valve returns to normal operation. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Coil Pump |  |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| FINAL FILTER SECTION |  |  |  |  |  |  |  |  |  |  |
|  | Activate the filter high pressure differential switch by applying pressure to the high side of the switch. | Dirty filter alarm indicated at BAS. |  |  | Filter Pressure at alarm _____________ in. WC |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial |  | Date |  |  |  |
|  | Release pressure from high side of switch and return to its normal condition. | Dirty filter alarm cleared at BAS. |  |  | Filter Pressure at alarm _____________ in. WC |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial |  | Date |  |  |  |
| HUMIDIFIER VALVES |  |  |  |  |  |  |  |  |  |  |
|  | Command humidifier isolation valve to fully close. Command humidifier control valve fully open. | Isolation valve closes. |  |  |  |  |  |  |  |  |
|  |  | Humidifier control valve fully opens. |  |  |  |  |  |  |  |  |
|  |  | No steam enters supply air stream. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command humidifier control valve fully closed. | Humidifier control valve fully closes. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command humidifier isolation valve fully open. | Humidifier isolation valve fully opens. |  |  |  |  |  |  |  |  |
|  |  | No steam is enters supply air stream. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command humidifier control valve 50% open. | Humidifier control valve opens 50%. |  |  |  |  |  |  |  |  |
|  |  | Steam begins entering supply air stream. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command humidifier control valve 100% open. | Humidifier control valve opens 100%. |  |  |  |  |  |  |  |  |
|  |  | Steam flow into supply air stream increases. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Remove power from the humidifier control valve and isolation valve. | Humidifier isolation valve moves to its fail safe position (fully closed). |  |  |  |  |  |  |  |  |
|  |  | Humidifier control valve moves to its fail safe position (fully closed). |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Release override on humidifier valves. | Humidifier valves return to normal operation. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| MULTIZONE COIL SECTION |  |  |  |  |  |  |  |  |  |  |
|  | Command hot deck heating coil control valve to 100% open. | Heating coil valve fully opens. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command hot deck heating coil control valve to close fully. | Heating coil valve fully closes. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command hot deck heating coil control valve to 50% open. | Heating coil control valve opens to 50%. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Remove power from the hot deck heating coil control valve actuator. | Heating coil control valve moves to its fail safe position (fully open). |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Release overrides on hot deck heating coil valve. | Preheat coil control valve returns to normal operation. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command cold deck coil control valve to 100% open. | Chilled water coil valve fully opens. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command cold deck coil control valve to close fully. | Chilled water coil valve fully closes. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command cold deck coil control valve to 50% open. | Chilled water coil control valve opens to 50%. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Remove power from the cold deck control valve actuator. | Chilled water coil control valve moves to its fail safe position (fully closed). |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Release override on cold deck coil valve. | Chilled water coil control valve returns to normal operation. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Coil Pump |  |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| MULTIZONE DAMPERS |  |  |  |  |  |  |  |  |  |  |
|  | Command hot and cold deck multizone dampers fully open. | Hot deck damper opens fully without binding for complete travel distance. |  |  | Number of Zones: _____ (Complete steps for each set of zones) |  |  |  |  |  |
|  |  | Status device indicates hot deck damper is fully open. |  |  |  |  |  |  |  |  |
|  |  | Cold deck damper opens fully without binding for complete travel distance. |  |  |  |  |  |  |  |  |
|  |  | Status device indicates cold deck damper is fully open. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Cold deck damper commanded to fully closed | Damper closes tightly without binding for complete travel distance. |  |  |  |  |  |  |  |  |
|  |  | Status device indicates damper is closed. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Cold deck damper commanded to 50% open | Damper opens half way without binding for complete travel distance. |  |  |  |  |  |  |  |  |
|  |  | Status device indicates damper is open. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Cold deck damper commanded fully open. After face damper confirmed open, bypass damper commanded fully closed. | Cold deck damper opens fully. |  |  |  |  |  |  |  |  |
|  |  | Hot deck damper closes tightly without binding for complete travel distance. |  |  |  |  |  |  |  |  |
|  |  | Status device indicates hot deck damper is closed. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Hot deck damper commanded to 50% open | Damper opens half way without binding for complete travel distance. |  |  |  |  |  |  |  |  |
|  |  | Status device indicates damper is open. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Release all damper overrides. | Dampers return to normal operating positions. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| SAFETIES AND INTERLOCKS |  |  |  |  |  |  |  |  |  |  |
| FREEZESTAT AND SYSTEM STARTUP |  |  |  |  |  |  |  |  |  |  |
|  | Apply aerosol spray to the serpentine temperature sensor (Freezestat). | Low temperature limit trips. |  |  |  |  |  |  |  |  |
|  |  | Supply fan VFD commanded to 0%. |  |  |  |  |  |  |  |  |
|  |  | Supply fan shuts down. |  |  |  |  |  |  |  |  |
|  |  | Outside air damper fully closes. |  |  |  |  |  |  |  |  |
|  |  | Fire smoke dampers close. |  |  |  |  |  |  |  |  |
|  |  | Humidifier is off and commanded to 0%. |  |  |  |  |  |  |  |  |
|  |  | Face and bypass damper modulates. |  |  |  |  |  |  |  |  |
|  |  | Preheat valve fully opens. |  |  |  |  |  |  |  |  |
|  |  | Cooling valve closed. |  |  |  |  |  |  |  |  |
|  |  | Low limit temperature alarm generated at BAS. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command the system Off | The system remains in the shutdown sequence. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Disconnect the power to the local control panel | Control panel is off. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | After 2-5 minutes reconnect power to the control panel (Control Panel Power Loss) | Control panel becomes operational upon restoration of power. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Command the system back ON (System Startup) | System remains shut down. |  |  | System requires manual reset of tripped device before air handling unit is restarted. |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Manually reset the Freezestat (System startup) | Outside air damper opens. |  |  | Minimum supply fan speed:_______ Duration fan at minimum speed:______ |  |  |  |  |  |
|  |  | Return air damper modulate as normal. |  |  |  |  |  |  |  |  |
|  |  | Supply fan VFD shall be commanded to run. |  |  |  |  |  |  |  |  |
|  |  | Supply fan turns ON at minimum speed for specified length of time. |  |  |  |  |  |  |  |  |
|  |  | Supply fan speed modulates to maintain differential pressure set-point. |  |  |  |  |  |  |  |  |
|  |  | Cooling valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Humidifier valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Preheat valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Face and bypass dampers is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Low limit temperature alarm clears at BAS. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| SUPPLY FAN FAILURE |  |  |  |  |  |  |  |  |  |  |
|  | At the local power disconnect or HOA switch, open the power loop to stop the fan. (Supply Fan Failure) | The supply fan turns off. |  |  |  |  |  |  |  |  |
|  |  | Supply fan failure alarm is generated at the BAS. |  |  |  |  |  |  |  |  |
|  |  | Fan isolation damper closed. |  |  |  |  |  |  |  |  |
|  |  | Outside air damper is closed. |  |  |  |  |  |  |  |  |
|  |  | Humidifier valve is closed. |  |  |  |  |  |  |  |  |
|  |  | Cooling coil valve is closed. |  |  |  |  |  |  |  |  |
|  |  | Preheat valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Face & Bypass damper is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Return/Exhaust Fan shuts down. |  |  |  |  |  |  |  |  |
|  |  | Wall mounted supply, return air isolation, unit mounted outdoor air dampers close fully. |  |  |  |  |  |  |  |  |
|  |  | Unit mounted return air dampers open. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | At the local power panel reconnect the disconnect or HOA switch, close the power loop to start the fan/fans. (Supply Fan Failure) | Outside air damper is open. |  |  |  |  |  |  |  |  |
|  |  | Wall mounted supply, return air isolation, unit mounted outdoor air dampers open. |  |  |  |  |  |  |  |  |
|  |  | Unit mounted return air dampers remain open. |  |  |  |  |  |  |  |  |
|  |  | The supply fan turns ON. |  |  |  |  |  |  |  |  |
|  |  | Supply fan failure alarm clears at the BAS. |  |  |  |  |  |  |  |  |
|  |  | Humidifier valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Cooling coil valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Preheat valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Face & Bypass damper is under BAS control. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| RETURN/EXHAUST FAN FAILURE |  |  |  |  |  |  |  |  |  |  |
|  | At the local power disconnect or HOA switch, open the power loop to stop the return/exhaust fan. | The return/exhaust fan turns off. |  |  |  |  |  |  |  |  |
|  |  | Fan isolation damper closed. |  |  |  |  |  |  |  |  |
|  |  | Current sensing relay indicates a loss of current from the component. |  |  |  |  |  |  |  |  |
|  |  | Return/Exhaust fan failure alarm generated at the BAS. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | At the local power disconnect or HOA switch, close the power loop to stop the return/exhaust fan. | The return/exhaust fan turns on. |  |  |  |  |  |  |  |  |
|  |  | Current sensing relay senses current from the component. |  |  |  |  |  |  |  |  |
|  |  | Return/Exhaust fan failure alarm cleared at the BAS. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| HIGH DUCT STATIC PRESSURE LIMIT SWITCH |  |  |  |  |  |  |  |  |  |  |
|  | Adjust the system shutdown high limit discharge air static pressure limit switch set-point to be just below the current discharge air static pressure or use a pump bulb and gauge to simulate high static conditions and record the setting. (High Pressure System Shutdown Alarm) | High static limit switch alarm is generated at BAS. |  |  | System Shutdown High Limit Switch Set-point: ___________ |  |  |  |  |  |
|  |  | The supply fan turns off. |  |  |  |  |  |  |  |  |
|  |  | Unit is indexed to Unoccupied Mode. |  |  |  |  |  |  |  |  |
|  |  | Smoke dampers are closed. |  |  |  |  |  |  |  |  |
|  |  | Outside air damper is closed. |  |  |  |  |  |  |  |  |
|  |  | Humidifier valve is closed. |  |  |  |  |  |  |  |  |
|  |  | Cooling coil valve is closed. |  |  |  |  |  |  |  |  |
|  |  | Preheat valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Face & Bypass damper is under BAS control. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Return the system shutdown high pressure limit switch set-point back to its original value or release the pump bulb pressure simulation | High pressure alarm is cleared at BAS. |  |  |  |  |  |  |  |  |
|  |  | System does not restart. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Manually reset the high pressure limit switch. | System restarts and resumes normal operation. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| LOW DUCT STATIC PRESSURE LIMIT SWITCH |  |  |  |  |  |  |  |  |  |  |
|  | Adjust the system shutdown low limit discharge air static pressure limit switch set-point to be just below the suction side static pressure or use a pump bulb and gauge to simulate low static conditions and record the setting. (Low Pressure System Shutdown Alarm) | Low static limit switch alarm is generated at BAS. |  |  | System Shutdown Low Limit Switch Set-point: ___________ |  |  |  |  |  |
|  |  | The supply fan turns off. |  |  |  |  |  |  |  |  |
|  |  | Unit is indexed to Unoccupied Mode. |  |  |  |  |  |  |  |  |
|  |  | Smoke dampers are closed. |  |  |  |  |  |  |  |  |
|  |  | Outside air damper is closed. |  |  |  |  |  |  |  |  |
|  |  | Humidifier valve is closed. |  |  |  |  |  |  |  |  |
|  |  | Cooling coil valve is closed. |  |  |  |  |  |  |  |  |
|  |  | Preheat valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Face & Bypass damper is under BAS control. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Return the system shutdown low pressure limit switch set-point back to its original value or release the pump bulb pressure simulation | Low pressure alarm is cleared at BAS. |  |  |  |  |  |  |  |  |
|  |  | System does not restart. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Manually reset the low pressure limit switch. | System restarts and resumes normal operation. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| DUCT SMOKE DETECTION |  |  |  |  |  |  |  |  |  |  |
|  | Apply aerosol smoke to the duct smoke detectors (Smoke Detection) | Smoke detection alarm is sent to the BAS. |  |  |  |  |  |  |  |  |
|  |  | The supply fan turns off. |  |  |  |  |  |  |  |  |
|  |  | Wall mounted supply, return air isolation, unit mounted outdoor air dampers close fully. |  |  |  |  |  |  |  |  |
|  |  | Unit mounted return air dampers open. |  |  |  |  |  |  |  |  |
|  |  | Outside air damper is closed. |  |  |  |  |  |  |  |  |
|  |  | Humidifier valve is closed. |  |  |  |  |  |  |  |  |
|  |  | Cooling coil valve is closed. |  |  |  |  |  |  |  |  |
|  |  | Preheat valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Face & Bypass damper is under BAS control. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Manually reset the smoke detector. (Smoke Detection) | Smoke detection alarm clears. |  |  |  |  |  |  |  |  |
|  |  | Wall mounted supply, return air isolation, unit mounted outdoor air dampers open fully. |  |  |  |  |  |  |  |  |
|  |  | Unit mounted return air dampers remain open. |  |  |  |  |  |  |  |  |
|  |  | Outside air damper opens. |  |  |  |  |  |  |  |  |
|  |  | Supply fan VFD shall be commanded to run. |  |  |  |  |  |  |  |  |
|  |  | Supply fan turns ON at minimum speed for a specified length of time. |  |  |  |  |  |  |  |  |
|  |  | Supply fan speed modulates to maintain differential pressure set-point. |  |  |  |  |  |  |  |  |
|  |  | Humidifier valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Cooling coil valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Preheat valve is under BAS control. |  |  |  |  |  |  |  |  |
|  |  | Face & Bypass damper is under BAS control. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| FUNCTIONAL TESTS – UNOCCUPIED NIGHT SETBACK – SETUP MODE |  |  |  |  |  |  |  |  |  |  |
|  | Modulate the outside air temperature for AHU # to be below 80°F | Return air damper closes to 10% minimum position. |  |  |  |  |  |  |  |  |
|  |  | Outside air damper opens to 90% maximum position. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Modulate the outside air temperature for AHU # to be above 80°F | Outside air damper closes to 10% minimum position. |  |  |  |  |  |  |  |  |
|  |  | Return air damper opens to 90% maximum position. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Adjust the discharge air temperature set-point to be 5°F lower than the current discharge air temperature for AHU # (Temperature Control Cooling) | (If the outside air temp is between 40°F and 80°F and the boiler room space temp is above 90°F). |  |  | Chiller room temperature set point: °F Discharge air temperature set-point: _____°F |  |  |  |  |  |
|  |  | Return air dampers and outside air dampers modulate in opposition to one another to maintain the 60°F set point. |  |  |  |  |  |  |  |  |
|  |  | Barometric relief dampers will relieve excess air from the boiler room. |  |  |  |  |  |  |  |  |
|  |  | Heating coil valves open. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Adjust the discharge air temperature set-point to be 10°F lower than the current discharge air temperature for AHU # (Temperature Control Cooling) | (If the outside air temp is below 90°F and the boiler room space temp is above 90°F). |  |  | Discharge air temperature set-point ______°F. |  |  |  |  |  |
|  |  | Return air dampers modulate open. |  |  |  |  |  |  |  |  |
|  |  | Outside air dampers modulate closed. |  |  |  |  |  |  |  |  |
|  |  | Barometric relief dampers will relieve excess air from the boiler room. |  |  |  |  |  |  |  |  |
|  |  | Heating coil valve closes. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | If the outside air temperature is above 40°F, override the outside air temperature reading to be 35°F for AHU #. Otherwise, skip this step. (At the end of this step, release the outside air temperature override) | Preheat valve is fully open. |  |  | This would indicate a situation where we could potentially simultaneously heat and cool. Please clarify the sequence that protects the system from simultaneously heating and cooling. |  |  |  |  |  |
|  |  | Cooling valve is open. |  |  |  |  |  |  |  |  |
|  |  | Face & bypass is modulated to maintain minimum air temperature set-point. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Reset the discharge air temperature set-point to the original value for AHU #. (Temperature Control Cooling) | The system resumes “normal” operations. |  |  | Ending discharge air temperature set-point _______°F |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Adjust the discharge air temperature, for AHU # set-point to be 5°F lower than the current discharge air temperature (Temperature Control Cooling) | (If the outside air temp is below 90°F and the boiler room space temp is above 90°F). |  |  | Boiler space temperature set point: °F Discharge air temperature set-point _____°F |  |  |  |  |  |
|  |  | Return air dampers modulate closed. |  |  |  |  |  |  |  |  |
|  |  | Outside air dampers modulate open. |  |  |  |  |  |  |  |  |
|  |  | Barometric relief dampers will relieve excess air from the boiler room. |  |  |  |  |  |  |  |  |
|  |  | Heating coil valves open |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Adjust the discharge air temperature set-point to be 10°F lower than the current discharge air temperature for AHU # (Temperature Control Cooling) | (If the outside air temp is below 90°F and the boiler room space temp is above 90°F). |  |  | Discharge air temperature set-point ______°F |  |  |  |  |  |
|  |  | Return air dampers modulate open. |  |  |  |  |  |  |  |  |
|  |  | Outside air dampers modulate closed. |  |  |  |  |  |  |  |  |
|  |  | Barometric relief dampers will relieve excess air from the boiler room. |  |  |  |  |  |  |  |  |
|  |  | Heating coil valve closes. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | If the outside air temperature is above 40°F, override the outside air temperature reading to be 35°F for AHU #. Otherwise, skip this step. (At the end of this step, release the outside air temperature override) | Preheat valve is fully open. |  |  | This would indicate a situation where we could potentially simultaneously heat and cool. Please clarify the sequence that protects the system from simultaneously heating and cooling. |  |  |  |  |  |
|  |  | Cooling valve is open |  |  |  |  |  |  |  |  |
|  |  | Face & bypass is modulated to maintain minimum air temperature set-point. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Reset the discharge air temperature set-point to the original value for AHU #. (Temperature Control Cooling) | The system resumes “normal” operations. |  |  | Ending discharge air temperature set-point _______F |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| FUNCTIONAL TESTS – UNOCCUPIED NIGHT SETBACK – SETUP MODE |  |  |  |  |  |  |  |  |  |  |
|  | Set discharge air temperature to less than 35°F. | Supply fan stops. |  |  | Initial Space Temp: __________ Space set point:__________ |  |  |  |  |  |
|  |  | Outside air damper closes. |  |  |  |  |  |  |  |  |
|  |  | Return air damper opens. |  |  |  |  |  |  |  |  |
|  |  | Alarm sent to BAS. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Reset discharge air temperature to original settings | Supply fan starts up. |  |  | New space temperature set point: __________ |  |  |  |  |  |
|  |  | Outside air damper opens. |  |  |  |  |  |  |  |  |
|  |  | Return air damper modulates as normal. |  |  |  |  |  |  |  |  |
|  |  | Alarm cleared from BAS. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Adjust the discharge air static pressure above the 0.02” w.c. set point in comparison to the outdoors --or-- Increase the discharge air static pressure set-point just under the high limit alarm discharge air static pressure set-point **Choose whichever results in a lower adjusted set-point and prevents high static alarm from sounding (Pressure Control) | The supply fan VFD increases the frequency and speeds up the fan to meet the new discharge air static pressure set-point. |  |  | Pressure of Outside: ___________ Static Pressure of Space: ___________ New Static Set-point:______ Frequency @ New Set-point:______% |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Adjust the high limit alarm discharge air static pressure set-point to be just below the current discharge air static pressure (High Pressure Alarm) | High static pressure alarm is generated. |  |  | New High Limit Static Alarm Set-point:___________ |  |  |  |  |  |
|  |  | Air handling system continues to run under BAS control. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Adjust the discharge air static pressure below the 0.02” w.c. set point in comparison to the outdoors --or-- Decrease the discharge air static pressure set-point just under the high limit alarm discharge air static pressure set-point **Choose whichever results in a higher adjusted set-point and prevents low static alarm from sounding (Pressure Control) | The supply fan VFD decreases the frequency and slows the fan to meet the new discharge air static pressure set-point. |  |  | Pressure of Outside: ___________ Static Pressure of Space: ___________ New Static Set-point:______ Frequency @ New Set-point:______% |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Adjust the low limit discharge air static pressure set-point to be just above the current discharge air static pressure (Low Pressure Alarm) | Low static pressure alarm is generated. |  |  | New Low Limit Static Set-point:_______ |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Return the low limit pressure alarm set-point back to its original value | The system resumes “normal” operation. |  |  | Low limit pressure alarm set-point:__________ Discharge air static pressure set-point:__________ |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Return the discharge air static pressure set-point back to its original value | The system resumes “normal” operation. |  |  | Low limit pressure alarm set-point:__________ Discharge air static pressure set-point:__________ |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| VERIFICATION OF UNOCCUPIED OPERATION |  |  |  |  |  |  |  |  |  |  |
|  | Override the occupancy to unoccupied | The supply fan is off. |  |  |  |  |  |  |  |  |
|  |  | The outside air damper is closed. |  |  |  |  |  |  |  |  |
|  |  | Return air damper opens. |  |  |  |  |  |  |  |  |
|  |  | The cooling coil valve is closed. |  |  |  |  |  |  |  |  |
|  |  | The preheat valve is closed. |  |  |  |  |  |  |  |  |
|  |  | Face and bypass damper is at full bypass. |  |  |  |  |  |  |  |  |
|  |  | The humidifier valve is closed. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Adjust the zone temperature set-point to 5F greater than the current temperature | The outside air damper is open. |  |  | Zone temperature set-point _______F |  |  |  |  |  |
|  |  | Return air dampers are open. |  |  |  |  |  |  |  |  |
|  |  | Supply fan VFD shall be commanded to run. |  |  |  |  |  |  |  |  |
|  |  | The supply fan turns on at minimum speed for a specified length of time. |  |  |  |  |  |  |  |  |
|  |  | Supply fan speed modulates to maintain differential pressure set-point. |  |  |  |  |  |  |  |  |
|  |  | The preheat valve modulates to meet the new set-point. |  |  |  |  |  |  |  |  |
|  |  | Face and bypass dampers are at full face. |  |  |  |  |  |  |  |  |
|  |  | Cooling coil valve is closed. |  |  |  |  |  |  |  |  |
|  |  | Humidifier valve is closed. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Adjust the zone temperature set-point to equal the current temperature | The supply fan turns off. |  |  | Zone temperature set-point ______F |  |  |  |  |  |
|  |  | The outside air damper closes. |  |  |  |  |  |  |  |  |
|  |  | Face and bypass dampers remain under BAS control. |  |  |  |  |  |  |  |  |
|  |  | The cooling coil valve is closed. |  |  |  |  |  |  |  |  |
|  |  | The humidifier valve is closed. |  |  |  |  |  |  |  |  |
|  |  | Unit is indexed back to the Unoccupied Mode. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Reset the schedule to occupied | The system resumes “normal” operation. |  |  | Ending zone temperature set-point ______F |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Reset the zone temperature set-point back to the original value | The system resumes “normal” operation. |  |  | Ending zone temperature set-point ______F |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| VERFICATION OF EXHAUST FAN |  |  |  |  |  |  |  |  |  |  |
|  | Set the airflow set point below the current air flow CFM | Alarm is sent to BAS. |  |  |  |  |  |  |  |  |
|  |  | Fan shuts off. |  |  |  |  |  |  |  |  |
|  |  | The discharge damper closes. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Reset the air flow set point to original set point though the BAS | Alarm clears. |  |  |  |  |  |  |  |  |
|  |  | The discharge damper opens. |  |  |  |  |  |  |  |  |
|  |  | The fan starts only when the damper is proved fully open. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Set static pressure set point above current static pressure | Low suction alarm is sent to BAS. |  |  |  |  |  |  |  |  |
|  |  | Fan shuts off. |  |  |  |  |  |  |  |  |
|  |  | Damper modulates open. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Reset the air flow set point to original set point though the BAS | Alarm clears. |  |  |  |  |  |  |  |  |
|  |  | The discharge damper stays open. |  |  |  |  |  |  |  |  |
|  |  | The fan starts only when the damper is proved fully open. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Reset the air flow set point to original set point though the BAS | Alarm clears. |  |  |  |  |  |  |  |  |
|  |  | The discharge damper stays open. |  |  |  |  |  |  |  |  |
|  |  | The fan starts only when the damper is proved fully open. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| RETURN TO INITIAL CONDITIONS |  |  |  |  |  |  |  |  |  |  |
|  | Record test stop time | Recorded. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |

| ## Final Sign-Off |  |  |  |  |
| --- | --- | --- | --- | --- |
| Commissioning Agent | Printed Name | Initials | Date |  |
| CONTRACTOR | PRINTED NAME | INITIALS | DATE |  |
| General Contractor (GC) |  |  |  |  |
| Mechanical Contractor (MC) |  |  |  |  |
| Electrical Contractor (EC) |  |  |  |  |
| TAB Contractor (TAB) |  |  |  |  |
| Controls Contractor (CC) |  |  |  |  |
| Owner’s O&M Personnel |  |  |  |  |