# Grounding & Bonding for Electrical Systems

# Functional Performance Test

| Equipment ID | [Equipment ID] |
| --- | --- |
| Building | {Building] |
| Location | [Room] |

## System Description

Description:

Operational Assumptions:

| Initial Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 1 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 2 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Deferred/Seasonal Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

## Test Participants

| Organization | Required | Optional |
| --- | --- | --- |
| General Contractor |  |  |
| Mechanical Contractor |  |  |
| Electrical Contractor |  |  |
| TAB Contractor |  |  |
| Controls Contractor |  |  |
| Owner’s O&M Personnel |  |  |

## Test Equipment Required (to be provided by the Contractor)

| Test Name | Equipment Description |
| --- | --- |
| Bolt Torque | Calibrated torque wrench |
| Contact Resistance | Four-probe Digital Low Resistance Ohmmeter (DLRO) |
| Voltage/Continuity | DVM |
| Fall of Potential | Fall-of-Potential Ground Resistance Tester |

## Functional Performance Test -- (Verify all components are ready before energizing or operating the system.)

The Commissioning Authority will make and document any changes/addition/deletions to this test procedure required by current system conditions (i.e. weather, system load, utility availability, etc.).

R = Retest (Check () retest required)								Y= Checked and Passed

C = Corrected (Check () when correction verified)					              N = Not Passed

| ACTION |  | REQUIRED REACTION | Y () | N () | COMMENTS |  | R () | C () |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PRE-TEST VISUAL MECHANICAL INSPECTION |  |  |  |  |  |  |  |  |
|  | Verify equipment identification. | Equipment identification and plan location matches shop drawings and specifications. |  |  |  |  |  |  |
|  |  | Field wiring terminations match record drawings. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Confirm that system is installed per contract documents with indicated connections to each unit of electrical equipment | Connections to equipment ground buses per drawings. |  |  |  |  |  |  |
|  |  | Connections to equipment enclosures/cases per drawings. |  |  |  |  |  |  |
|  |  | Connections to wire mesh fence per drawings. |  |  |  |  |  |  |
|  |  | Gate grounding jumper installed per drawings. |  |  |  |  |  |  |
|  |  | Connections to main cold water pipes per drawings and specs. |  |  |  |  |  |  |
|  |  | Connections to dry type transformers per drawings and specs. |  |  |  |  |  |  |
|  |  | Measured diameter of bare copper conductor corresponds to diameter of specified conductors. |  |  |  |  |  |  |
|  |  | Conduits with grounding bushings and full-size bonding conductors. |  |  |  |  |  |  |
|  |  | All busses mounted on standoff neoprene insulators. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Observe condition of ground ring before backfill and/or cover applied. | No visible damage to cable. |  |  |  |  |  |  |
|  |  | Cable depth a minimum of 3’0”. |  |  |  |  |  |  |
|  |  | Ground rod configuration and depth as shown on drawings. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Observe main ground wall mounted grounding bar. | Dimensions as specified ____ long, 4” x ¼”. |  |  |  |  |  |  |
|  |  | Standoff distance 5” from wall as shown on drawings. |  |  |  |  |  |  |
|  |  | Connections are welded or bolted as per the approved submittals and construction drawings. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Observe electrical closet ground buses | Buses: Copper, ¼” x 2” x10” minimum, length as shown on drawings. |  |  |  |  |  |  |
|  |  | Buses mounted on standoff neoprene insulator - standoff distance 1” from wall as shown on drawings. |  |  |  |  |  |  |
|  |  | Bus length to accommodate 100% spare. |  |  |  |  |  |  |
|  |  | Connections are welded or bolted as per the approved submittals and construction drawings. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Observe telecom closet ground buses | Buses: Copper, ¼” x 2” x8” provided by each telecom backboard. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Inspect compression type and exothermically welded connections | Cables do not rotate with respect to each other or to steel column, etc. (All connections are solid). |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Inspect grounding connection at service entrance | Connection point is per (not beyond service disconnect) NEC 250-23. |  |  |  |  |  |  |
|  |  | Neutral is solidly grounded at service disconnect, and at no point beyond. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Verify equipment grounding conductor termination. | Grounding connections are made with non-reversible connections. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Verify tightness of accessible bolted electrical connections with calibrated torque wrench. | Bolted torque should comply with NETA Table 100.12 unless manufacturer specified values are listed on the equipment. |  |  | Record data in Contact Integrity Table Bolt Torque |  |  |  |
|  |  | If Contractor’s Test Reports are received and used in lieu of 100% testing, perform random checks of tightness of bolted electrical connections. Randomly Test 10% of connections. If any are not tight, test 100%. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
| GROUNGING ELECTRICAL INTEGRITY |  |  |  |  |  |  |  |  |
|  | Perform resistance test of non-accessible bolted electrical system connections using a Digital Low Resistance Ohmmeter (DLRO) and non-bolted electrical system connections using a DVM. | Resistance shall be less than 500 micro-ohms. |  |  | Note: For connections that are inaccessible or unable to be verified by torque (ex: welded connections), conduct a DLRO measurement of connection resistance across connection from closest accessible point on each side. Record Data in Contact Integrity Table – DLRO/DVM |  |  |  |
|  |  | Compare connection resistance to values of similar connections. Values should be within 10% of each other. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Verify the ground system is complete (connections to building steel, water main etc.) and tested prior to performing the final “system” fall of potential. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Perform and evaluate a Fall-of-Potential test on the grounding system. | The curve should be “flat” between Y1 and Y2 |  |  | The fall of potential test consists of plotting the ratio of V/I-R as a function of probe spacing. A value of impedance is obtained at Y, Y1 and Y2. This impedance is plotted as a function of distance, and the value in ohms at which this plotted curve appears to level out is taken as the impedance value of the ground under test. If the curve is not flat between Y1 and Y2 additional impedance measurements must be taken. Position the potential probe at several additional distances between the electrode and current probe Z. Record distances and plots the impedance to obtain the flat area of the curve. Attach a copy of the Fall-of-Potential contractor’s test report on all individual ground rods. Record values in Fall of Potential Table. |  |  |  |
|  |  | The resistance value at distance Y is effective resistance of the electrode or system. |  |  |  |  |  |  |
|  |  | Results are less than or equal to 10 ohms. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |

## Test Equipment Used:

| Test Name | Manufacturer | Model Number | Serial Number | Calibration (Date) |
| --- | --- | --- | --- | --- |

Connection Integrity

| Conductor Description |  | Torque Verified |  | DLRO/DVM |  | Continuity Verified | Date |
| --- | --- | --- | --- | --- | --- | --- | --- |
| # From (A) | To (B) | (A) | (B) | (A) | (B) |  |  |

Fall of Potential

| Electrode ID | Distance (Y1) | Distance Y | Distance (Y2) | Distance (Z) | Resistance | AT | RH | Date |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

AT=Ambient Temperature

RH = Relative Humidity

| ## Final Sign-Off |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Commissioning Agent | Printed Name |  | Initials | Date |  |
| CONTRACTOR | PRINTED NAME |  | INITIALS | DATE |  |
| General Contractor (GC) |  |  |  |  |  |
| Mechanical Contractor (MC) |  |  |  |  |  |
| Electrical Contractor (EC) |  |  |  |  |  |
| TAB Contractor (TAB) |  |  |  |  |  |
| Controls Contractor (CC) |  |  |  |  |  |
| Owner’s O&M Personnel |  |  |  |  |  |

TABLE 100.12.1

Bolt-Torque Values for Electrical Connections

US Standard Fasteners a
Heat-Treated Steel – Cadmium or Zinc Plated b

| Grade | SAE 1&2 |  |  |  | SAE 5 |  |  | SAE 7 |  | SAE 8 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Head Marking |  |  |  |  |  |  |  |  |  |  |  |
| Minimum Tensile (Strength) (lbf/in2) | 64K |  |  |  | 105K |  |  | 133K |  | 150K |  |
| Bolt Diameter (Inches) |  |  | Torque (Pound-Feet) |  |  |  |  |  |  |  |  |
| 1/4 |  | 4 |  |  |  | 6 |  |  | 8 |  | 8 |
| 5/16 |  | 7 |  |  |  | 11 |  |  | 15 |  | 18 |
| 3/8 |  | 12 |  |  |  | 20 |  |  | 27 |  | 30 |
| 7/16 |  | 19 |  |  |  | 32 |  |  | 44 |  | 48 |
| 1/2 |  | 30 |  |  |  | 48 |  |  | 68 |  | 74 |
| 9/16 |  | 42 |  |  |  | 70 |  |  | 96 |  | 105 |
| 5/8 |  | 59 |  |  |  | 96 |  |  | 135 |  | 145 |
| 3/4 |  | 96 |  |  |  | 160 |  |  | 225 |  | 235 |
| 7/8 |  | 150 |  |  |  | 240 |  |  | 350 |  | 380 |
| 1.0 |  | 225 |  |  |  | 370 |  |  | 530 |  | 570 |

- Consult manufacturer for equipment supplied with metric fasteners.

- Table is based on national coarse thread pitch.