# Low-Voltage Switchgear

# Functional Performance Test

| Equipment ID | [Equipment ID] |
| --- | --- |
| Building | [Building] |
| Location | [Room] |

## System Description

Description:

Operational Assumptions:

| Initial Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 1 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 2 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Deferred/Seasonal Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

## Test Participants

| Organization | Required | Optional |
| --- | --- | --- |
| General Contractor |  |  |
| Mechanical Contractor |  |  |
| Electrical Contractor |  |  |
| TAB Contractor |  |  |
| Controls Contractor |  |  |
| Owner’s O&M Personnel |  |  |

## Test Instruments (To Be Provided By the Contractor)

Recommended Test Equipment (or Equivalent):

| Test | # Equipment Description |
| --- | --- |
| Bolt Torque | Calibrated torque wrench |
| Wiring Impedance | Low impedance ac millammeter |
| Sound Level | Calibrated decibel meter |

## System Readiness Summary Checklist

| Description | Yes | No | Date |
| --- | --- | --- | --- |
| System Ready for Test |  |  |  |
| Required Personnel Available |  |  |  |
| Required Tools/Test Equipment/Supplies Available |  |  |  |
| Required Safety Equipment Available |  |  |  |

## Functional Performance Test -- (Verify all components are ready before energizing or operating the system.)

The Commissioning Authority will make and document any changes/addition/deletions to this test procedure required by current system conditions (i.e. weather, system load, utility availability, etc.).

R = Retest (Check () retest required)								Y= Checked and Passed

C = Corrected (Check () when correction verified)					              N = Not Passed

| ACTION |  | REQUIRED REACTION | Y () | N () | COMMENTS |  | R () |  | C () |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PRE-TEST VISUAL MECHANICAL INSPECTION |  |  |  |  |  |  |  |  |  |
|  | Safe conditions (protective gear in-place, available & procedures observed) |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify panelboard installations | Isolation transformer installed with electrostatic shield between primary and secondary winding and connected to ground. |  |  |  |  |  |  |  |
|  |  | Completed panelboard schedules. |  |  |  |  |  |  |  |
|  |  | Appropriate anchorage. |  |  |  |  |  |  |  |
|  |  | Required area clearances. 3 ft in front and 30 in wide. |  |  |  |  |  |  |  |
|  |  | No physical damage. |  |  |  |  |  |  |  |
|  |  | Breaker casing does not have cracks. |  |  |  |  |  |  |  |
|  |  | Correct alignment. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Inspect panelboard doors, panels, and sections | Free of Corrosion, dents, scratches, fit. |  |  |  |  |  |  |  |
|  |  | No missing screws. |  |  |  |  |  |  |  |
|  |  | No open unused knockouts. |  |  |  |  |  |  |  |
|  |  | No missing hardware. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify panelboard configuration and nameplate data matches shop drawings, one-line diagram and specification | Volts:______. |  |  |  |  |  |  |  |
|  |  | Bus Amps: _____A. |  |  |  |  |  |  |  |
|  |  | 3ph, 4W. |  |  |  |  |  |  |  |
|  |  | Frequency: 60hZ. |  |  |  |  |  |  |  |
|  |  | Enclosure: ______. |  |  |  |  |  |  |  |
|  |  | Transformer _____KVA. |  |  |  |  |  |  |  |
|  |  | Transformer _____V. |  |  |  |  |  |  |  |
|  |  | Transformer class _____ insulation rating. |  |  |  |  |  |  |  |
|  |  | Transformer 60Hz. |  |  |  |  |  |  |  |
|  |  | Main Breaker Max. Rating. ____ Amp. |  |  |  |  |  |  |  |
|  |  | Panelboard arrangement _____# of circuits. |  |  |  |  |  |  |  |
|  |  | ______ Percent Spares. |  |  |  |  |  |  |  |
|  |  | ______ Space. |  |  |  |  |  |  |  |
|  |  | Neutral size _______. |  |  |  |  |  |  |  |
|  |  | LIM installed provides continuous monitoring of impedance of each phase to ground. |  |  |  |  |  |  |  |
|  |  | LIM combined analog and digital display. |  |  |  |  |  |  |  |
|  |  | LIM capable of detecting all combinations of capacitive, resistive, balanced, unbalanced and hybrid faults. |  |  |  |  |  |  |  |
|  |  | LIM contains audible alarm and alarm silence button. |  |  |  |  |  |  |  |
|  |  | LIM contains Indication LEDs. |  |  |  |  |  |  |  |
|  |  | LIM contains Test Button. |  |  |  |  |  |  |  |
|  |  | LIM contains remote terminal connections. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify panelboard equipment grounding | Solid neutral mounted in main circuit breaker compartment with main lugs, is insulated. |  |  |  |  |  |  |  |
|  |  | Neutral is bonded to ground. |  |  |  |  |  |  |  |
|  |  | Frame and enclosure connected to ground bus. |  |  |  |  |  |  |  |
|  |  | Breaker and feeder equipment grounding conductors/conduit are connected to ground bus. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | After testing is performed on the panelboard, verify tightness of main connections | Primary feeder cable connections properly torqued and marked. |  |  | Bolted torque should comply with NETA Table 100.12 unless manufacturer specified values are listed on the equipment. Test Name: Feeder Termination Torque Reference Equip. Table |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| CAUTION: Before performing the next step, verify that all “Lock-Out / Tag-Out” safety precautions have been adhered to. |  |  |  |  |  |  |  |  |  |
|  | Operate each circuit breaker (5) times to ensure smooth operation | Breaker opens and closes in a smooth motion without binding. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| ELECTRICAL INTEGRITY |  |  |  |  |  |  |  |  |  |
|  | Measure sound level of isolation transformer | 25bB for 5kVA or less transformer. |  |  | Test Name: Sound level Reference Equip. Table |  |  |  |  |
|  |  | 30dB for 7.5 kVA transformer. |  |  |  |  |  |  |  |
|  |  | 35dB for 10 and 15kVA transformers. |  |  |  |  |  |  |  |
|  |  | 40dBfor 20 and 25kVA transformers. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Perform continuity check on each branch circuit | Correct continuity is verified. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Measure each isolated wiring impedance to ground | Impedance shall exceed 200,000 ohms. |  |  | Test Name: Wire Impedance Reference Equip. Table Record results as a reference for subsequent line-impedance evaluation. Record results in Data Table |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| LINE ISOLATION MONITOR |  |  |  |  |  |  |  |  |  |
|  | Isolation power panel is in normal operation | Green signaling lamp is indicated on the panel. |  |  |  |  |  |  |  |
|  |  | Green signal shall be indicated at the remote monitoring station. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Ground each line of the energized distribution system through a resistor 200 times the measured line voltage | Red signaling lamp is illuminated and local alarm is annunciated. |  |  | Record results in Data Table |  |  |  |  |
|  |  | Green signal shall be indicated at the remote monitoring station. |  |  |  |  |  |  |  |
|  |  | Alarm resets automatically after ground is removed. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | During each line grounding test press the audible alarm silence button | Local and Remote Audible alarm silences. |  |  | Record results in Data Table |  |  |  |  |
|  |  | Local and Remote Red indicating light remains illuminated. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Activate test switch | Red signaling lamp is illuminated and local alarm is annunciated. |  |  |  |  |  |  |  |
|  |  | Red signal shall be indicated at the remote monitoring station. |  |  |  |  |  |  |  |
|  |  | Alarm resets automatically after release of test switch. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| FINAL INSPECTION |  |  |  |  |  |  |  |  |  |
|  | At the conclusion of testing, inspect interior hardware and electrical terminations | All hardware in place and properly torqued. |  |  |  |  |  |  |  |
|  |  | Compartments clear of tools and hardware. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |

## Test Equipment Used:

| Test Name | Manufacturer | Model Number | Serial Number | Calibration (Date) |
| --- | --- | --- | --- | --- |

## Panel Data

| Parameter | Data |
| --- | --- |
| Equipment ID: |  |
| Manufacturer: |  |
| Model Number: |  |
| Serial Number: |  |
| Mfgr. Date: |  |
| Bus Amps: |  |
| Volts: |  |
| Phase/Wire/Frequency: |  |
| Enclosure NEMA Rating: |  |
| Short Circuit Rating: |  |
| Isolation Transformer KVA |  |
| Isolation Transformer Voltage |  |
| LIM Manufacturer |  |

## Feeder Termination Torque (Newton Meters or Foot-Pounds)

| ## Bolt or Lug | ## A | ## B | ## C | ## N | ## G |
| --- | --- | --- | --- | --- | --- |
| ## Feeder Lugs |  |  |  |  |  |
| ## Feeder Lugs |  |  |  |  |  |

Sound Level

| Transformer | ________ KVA | Sound Level (Decibel) |
| --- | --- | --- |

## Wire Impedance (200,000 OHMS)

| Conductor |  | Torque Verified |  | DLRO/DVM |  | Continuity Verified | Date |
| --- | --- | --- | --- | --- | --- | --- | --- |
| From (A) | To (B) | (A) | (B) | (A) | (B) |  |  |

| Conductor | Volts | Resistor | Alarm Test |  |  |  | Alarm Silence |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Local Light (On/Off) | Local Audible (On/Off) | Remote Lights (On/Off) | Alarm Resets (On/Off) | Audible |  | Alarm Light |  |
|  |  |  |  |  |  |  | Local (On/Off) | Remote (On/Off) | Local (On/Off) | Remote (On/Off) |

| ## Final Sign-Off |  |  |  |  |
| --- | --- | --- | --- | --- |
| Commissioning Agent | Printed Name | Initials | Date |  |
| CONTRACTOR | PRINTED NAME | INITIALS | DATE |  |
| General Contractor (GC) |  |  |  |  |
| Mechanical Contractor (MC) |  |  |  |  |
| Electrical Contractor (EC) |  |  |  |  |
| TAB Contractor (TAB) |  |  |  |  |
| Controls Contractor (CC) |  |  |  |  |
| Owner’s O&M Personnel |  |  |  |  |