# Panelboards

# Functional Performance Test

| Equipment ID | [Equipment ID] |
| --- | --- |
| Building | [Building] |
| Location | [Room] |

## System Description

Description:

Operational Assumptions:

| Initial Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 1 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 2 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Deferred/Seasonal Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

## Test Equipment Required (to be provided by the Contractor)

| Test Name | Equipment Description |
| --- | --- |
| Bolt Torque | Calibrated torque wrench |
| Voltage/Continuity | DVM |
| Insulation Resistance | Battery or line-powered (Hand-crank not acceptable). |
| Variable Voltage Source | 3-Phase variable voltage source |

## Test Participants

| Organization | Required | Optional |
| --- | --- | --- |
| General Contractor |  |  |
| Mechanical Contractor |  |  |
| Electrical Contractor |  |  |
| TAB Contractor |  |  |
| Controls Contractor |  |  |
| Owner’s O&M Personnel |  |  |

## Functional Performance Test -- (Verify all components are ready before energizing or operating the system.)

The Commissioning Authority will make and document any changes/addition/deletions to this test procedure required by current system conditions (i.e. weather, system load, utility availability, etc.).

R = Retest (Check () retest required)								Y= Checked and Passed

C = Corrected (Check () when correction verified)					              N = Not Passed

| ACTION |  | REQUIRED REACTION | Y () | N () | COMMENTS |  | R () | C () |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PRE-TEST VISUAL MECHANICAL INSPECTION |  |  |  |  |  |  |  |  |
|  | Safe conditions (protective gear in-place, available & procedures observed) |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Verify panelboard installations | Completed panelboard schedules. |  |  |  |  |  |  |
|  |  | Appropriate anchorage. |  |  |  |  |  |  |
|  |  | Required area clearances. 3 ft in front and 30 in wide. |  |  |  |  |  |  |
|  |  | No physical damage. |  |  |  |  |  |  |
|  |  | Breaker casing does not have cracks. |  |  |  |  |  |  |
|  |  | Correct alignment. |  |  |  |  |  |  |
|  |  | Feeder color-coding is: 480/277 V System as follows: Phase A: Brown Phase B: Orange Phase C: Yellow Neutral: Gray Ground: Green |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Inspect panelboard doors, panels, and sections | Free of Corrosion, dents, scratches, fit. |  |  |  |  |  |  |
|  |  | No missing hardware. |  |  |  |  |  |  |
|  |  | No missing screws. |  |  |  |  |  |  |
|  |  | No open unused knockouts. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Verify panelboard configuration and nameplate data matches shop drawings, one-line diagram and specification | Volts: 480/277V. |  |  |  |  |  |  |
|  |  | Bus Amps: _____A. |  |  |  |  |  |  |
|  |  | 3ph, 4W. |  |  |  |  |  |  |
|  |  | Frequency: 60hZ. |  |  |  |  |  |  |
|  |  | Enclosure: NEMA 1. |  |  |  |  |  |  |
|  |  | Main Breaker Max. Rating. ____ Amp. |  |  |  |  |  |  |
|  |  | Isolated Equipment Ground Bus if applicable. |  |  |  |  |  |  |
|  |  | Panelboard arrangement - # of circuits. |  |  |  |  |  |  |
|  |  | Neutral bus size (100%). |  |  |  |  |  |  |
|  |  | Extra Gutter space as applicable. |  |  |  |  |  |  |
|  |  | Shunt trip as indicated. |  |  |  |  |  |  |
|  |  | TVSS as indicated. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Verify panelboard equipment grounding | Solid neutral mounted in main circuit breaker compartment with main lugs, is insulated. |  |  |  |  |  |  |
|  |  | Neutral is not bonded to ground. |  |  |  |  |  |  |
|  |  | Frame and enclosure connected to ground bus. |  |  |  |  |  |  |
|  |  | Breaker and feeder equipment grounding conductors/conduit are connected to ground bus. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Operate each circuit breaker (5) times to ensure smooth operation | Breaker opens and closes in a smooth motion without binding. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
| ELECTRICAL INTEGRITY |  |  |  |  |  |  |  |  |
|  | Perform an insulation resistance test at 1000VDC, phase-to-phase and phase to ground, in accordance with NETA Table 100.1 | Minimum insulation resistance shall be 100 Megohms. |  |  | Record results in Insulation Resistance Table. Perform the test on each bus section. Test for one minute in accordance with NETA Table 100.1. |  |  |  |
|  |  | Results temperature corrected in accordance with NETA Table 100.14. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Perform an insulation resistance test at 1000VDC on main breaker, phase-to-phase and phase to ground, connected to the bus in the CLOSED position, in accordance with NETA Table 100.1. Perform insulation resistance test (pole to pole) on main breaker with breaker in the open position | Minimum insulation resistance shall be 100 Megohms. |  |  | Record results in Insulation Resistance Table. Perform the test on each bus section. Test for one minute in accordance with NETA Table 100.1. Test Name: Insulation Resistance Reference Equip. Table |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | At the conclusion of testing, inspect interior hardware and electrical terminations | All hardware in place and properly torqued. |  |  |  |  |  |  |
|  |  | Compartments clear of tools and hardware. |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
| FUNCTIONAL TRIP TESTS |  |  |  |  |  |  |  |  |
|  | Test the Long Time Delay (seconds) and Long Time Pickup current (amperes) setting on device breakers rated 400A and greater, by using primary current injection | Long delay current pick up and time delay per coordination study. |  |  | Record results in Data Table. Test Name: Primary Current Inject. Reference Equip. Table |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Test the Short Time Delay (seconds) and Short Time Pickup current (amperes) setting on device breakers rated 400A and greater, by using primary current injection | Short delay current pick up and time delay per coordination study. |  |  | Record results in the Circuit Breaker Current Injection Table. Test Name: Primary Current Inject. Reference Equip. Table |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Test the Instantaneous Time Delay (seconds) and Instantaneous Time Pickup current (amperes) setting on device breakers rated 400A and greater, by using primary current injection | Instantaneous pick up per coordination study. |  |  | Record results in the Circuit Breaker Current Injection Table. Test Name: Primary Current Inject. Reference Equip. Table |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | Test the Ground Fault Time Delay (seconds) and Ground Fault Time Pickup current (amperes) setting on device breakers rated 400A and greater, by using primary current injection. | Ground fault pick up per coordination study. |  |  | Record results in the Circuit Breaker Current Injection Table. Test Name: Primary Current Inject. Reference Equip. Table |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |
|  | After testing is performed on the panelboard, verify tightness of main connections. | Primary feeder cable connections properly torqued and marked. |  |  | Record results in the Termination Torque Table. Bolted torque should comply with NETA Table 100.12 unless manufacturer specified values are listed on the equipment. Test Name: Bolt Torque Reference Equip. Table |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |

## Test Equipment Used:

| Test Name | Manufacturer | Model Number | Serial Number | Calibration (Date) |
| --- | --- | --- | --- | --- |

Data Tables

Temperature: ____________		Relative Humidity: ____________

Insulation Resistance (1000 VDC)

| Circuit Breaker (Closed) | A-B | B-C | C-A | A-G | B-G | C-G | N |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 Minute (Meg Ohms) |  |  |  |  |  |  |  |
| Circuit Breaker (open) | A-A | B-B | C-C |  |  |  |  |
| 1 Minute (Meg Ohms) |  |  |  |  |  |  |  |

Current Injection

| Function | Actual Set. | Test Setting | Test Point | Nominal Val. | A | B | C | Trip Setting (Sec.) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| LTD |  |  |  |  |  |  |  |  |
| LDPU |  |  |  |  |  |  |  |  |
| STD |  |  |  |  |  |  |  |  |
| SDPU |  |  |  |  |  |  |  |  |
| INSTPU |  |  |  |  |  |  |  |  |
| GFD |  |  |  |  |  |  |  |  |
| GFPU |  |  |  |  |  |  |  |  |

Termination Torque (Newton Meters or Foot Pounds)

| Bolt/Lug | A | B | C | N | G |
| --- | --- | --- | --- | --- | --- |
| Primary Feeder |  |  |  |  |  |
| Feeder Lugs |  |  |  |  |  |

| ## Final Sign-Off |  |  |  |  |
| --- | --- | --- | --- | --- |
| Commissioning Agent | Printed Name | Initials | Date |  |
| CONTRACTOR | PRINTED NAME | INITIALS | DATE |  |
| General Contractor (GC) |  |  |  |  |
| Mechanical Contractor (MC) |  |  |  |  |
| Electrical Contractor (EC) |  |  |  |  |
| TAB Contractor (TAB) |  |  |  |  |
| Controls Contractor (CC) |  |  |  |  |
| Owner’s O&M Personnel |  |  |  |  |

Table 100.1

Insulation Resistance Test Values

Electrical Apparatus and Systems

| Nominal Rating of Equipment in Volts | Minimum Test Voltage, DC | Recommended Minimum Insulation Resistance in Megohms |
| --- | --- | --- |
| 250 | 500 | 25 |
| 600 | 1,000 | 100 |
| 1,000 | 1,000 | 100 |
| 2,500 | 1,000 | 500 |
| 5,000 | 2,500 | 1,000 |
| 8,000 | 2,500 | 2,000 |
| 15,000 | 2,500 | 5,000 |
| 25,000 | 5,000 | 20,000 |
| 34,500 and above | 15,000 | 100,000 |

See Table 100.14 for temperature correction.

In the absence of consensus standards dealing with insulation-resistance tests, the Standards Review Council suggests the above representative values.

Test results are dependent on the temperature of the insulating material and the humidity of the surrounding environment at the time of the test.

Insulation-resistance test data may be used to establish a trending pattern.  Deviations from the baseline information permit evaluation of the insulation.

Table 100.12

US Standard

Bolt Torques for Bus Connection

Heat-Treated Steel – Cadmium or Zinc Plated

| Grade | SAE 1&2 | SAE 5 | SAE 7 | SAE 8 |
| --- | --- | --- | --- | --- |
| Head Markings |  |  |  |  |
| Minimum Tensile (P.S.I.) | 64K | 105K | 133K | 150K |
| Bolt Diameter in Inches | Torque (Foot Pounds) |  |  |  |
| 1/4 | 4.0 | 5.6 | 8.0 | 8.4 |
| 5/16 | 7.2 | 11.2 | 15.2 | 17.6 |
| 3/8 | 12.0 | 20.0 | 27.2 | 29.6 |
| 7/16 | 19.2 | 32.0 | 44.0 | 48.0 |
| 1/2 | 29.6 | 48.0 | 68.0 | 73.6 |
| 9/16 | 42.4 | 70.4 | 96.0 | 105.6 |
| 5/8 | 59.2 | 96.0 | 133.6 | 144.0 |
| 3/4 | 96.0 | 160.0 | 224.0 | 236.8 |
| 7/8 | 152.0 | 241.6 | 352.0 | 378.4 |
| 1.0 | 225.6 | 372.8 | 528.0 | 571.2 |

Reference:  International Electrical Testing Association (NETA) ATS-1999, Table 100.12, page 202.

Table 100.12 (Cont.)

Bolt Torques for Bus Connections

Silicon Bronze Fasteners1

Torque (Foot Pounds)

| Bolt Diameter in Inches | Nonlubricated | Lubricated |
| --- | --- | --- |
| 5/16 | 15 | 10 |
| 3/8 | 20 | 14 |
| 1/2 | 40 | 25 |
| 5/8 | 55 | 40 |
| 3/4 | 70 | 60 |

Reference:  International Electrical Testing Association (NETA) ATS-1999, Table 100.12, page 203.

Table 100.12 (Cont.)

Bolt Torques for Bus Connections

Aluminum Alloy Fasteners2

Torque (Foot Pounds)

| Bolt Diameter in Inches | Nonlubricated | Lubricated |
| --- | --- | --- |
| 5/16 | 15 | 8.0 |
| 3/8 | 20 | 11.2 |
| 1/2 | 40 | 20.0 |
| 5/8 | 55 | 32.0 |
| 3/4 | 70 | 48.0 |

Reference:  International Electrical Testing Association (NETA) ATS-1999, Table 100.12, page 203.

Table 100.12 (Cont.)

Bolt Torques for Bus Connections

Stainless Steel Fasteners3

Torque (Foot Pounds

| Bolt Diameter in Inches | Uncoated |
| --- | --- |
| 5/16 | 14 |
| 3/8 | 25 |
| 1/2 | 45 |
| 5/8 | 60 |
| 3/4 | 90 |

Reference:  International Electrical Testing Association (NETA) ATS-1999, Table 100.12, page 204.

Table 100.14

Insulation Resistance

Correction Factors

For Conversion of Test Temperature to 20˚C

| Temperature |  | Multiplier |  |
| --- | --- | --- | --- |
| ˚C | ˚F | Apparatus Containing Immersed Oil Insulations | Apparatus Containing Solid Insulators |
| 0 | 32 | 0.25 | 0.40 |
| 5 | 41 | 0.36 | 0.45 |
| 10 | 50 | 0.50 | 0.50 |
| 15 | 59 | 0.75 | 0.75 |
| 20 | 68 | 1.00 | 1.00 |
| 25 | 77 | 1.40 | 1.30 |
| 30 | 86 | 1.98 | 1.60 |
| 35 | 95 | 2.80 | 2.05 |
| 40 | 104 | 3.95 | 2.50 |
| 45 | 113 | 5.60 | 3.25 |
| 50 | 122 | 7.85 | 4.00 |
| 55 | 131 | 11.20 | 5.20 |
| 60 | 140 | 15.85 | 6.40 |
| 65 | 149 | 22.40 | 8.70 |
| 70 | 158 | 31.75 | 10.00 |
| 75 | 167 | 44.70 | 13.00 |
| 80 | 176 | 63.50 | 16.00 |

Reference:  International Electrical Testing Association (NETA) ATS-1999, Table 100.14, page 206.