# Engine Generators

# Functional Performance Test

| Equipment ID | [Equipment ID] |
| --- | --- |
| Building | [Building] |
| Location | [Room] |

## System Description

Description:

Operational Assumptions: Breaker Coordination study is available and includes the generator output breaker(s).

| Initial Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 1 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 2 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Deferred/Seasonal Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

## Test Participants

| Organization | Required | Optional |
| --- | --- | --- |
| General Contractor |  |  |
| Mechanical Contractor |  |  |
| Electrical Contractor |  |  |
| TAB Contractor |  |  |
| Controls Contractor |  |  |
| Owner’s O&M Personnel |  |  |

Test Equipment Required (to be provided by the Contractor)

| Test Name | Equipment Description |
| --- | --- |
| Voltage/Continuity | DVM |
| Bolted Connection or Contact Resistance | Four-probe Digital Low Resistance Ohmmeter (DLRO) |
| Insulation Resistance | Battery or line-powered (Hand-crank not acceptable). |
| Primary Current Injection | Current Injection Test Device rated for 2X the ground fault pickup setting of the breaker |
| 2 and 4 Hour Load Bank Test | Resistive load bank with capacity equal to or greater than rated load. Rated at 2% accuracy for voltage, current and KW. |
| Phase Rotation | Verify proper phasing |
| Volt. & Freq. Regulation | Computer to record voltage and frequency from the output of the generator control panel. |
| Decibel | Measure sound pressure |
| Back Pressure | Manometer with a scale of greater than 40” water |
| Bolt Torque | Calibrated torque wrench |

## System Readiness Summary Checklist

| Description | Yes | No | Date |
| --- | --- | --- | --- |
| System Ready for Test |  |  |  |
| Required Personnel Available |  |  |  |
| Required Tools/Test Equipment/Supplies Available |  |  |  |
| Required Safety Equipment Available |  |  |  |

## Functional Performance Test -- (Verify all components are ready before energizing or operating the system.)

The Commissioning Authority will make and document any changes/addition/deletions to this test procedure required by current system conditions (i.e. weather, system load, utility availability, etc.).

R = Retest (Check () retest required)								Y= Checked and Passed

C = Corrected (Check () when correction verified)					              N = Not Passed

| ACTION |  | REQUIRED REACTION | Y () | N () | COMMENTS |  | R () |  | C () |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PRE-TEST VISUAL MECHANICAL INSPECTION |  |  |  |  |  |  |  |  |  |
|  | Safe conditions (protective gear in-place, available & procedures observed) |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify that the Engine, Generator, Battery, and Battery Charger nameplate data matches shop drawings and construction documents. | kW: ______. |  |  | Record results in data table. |  |  |  |  |
|  |  | Rating: _______________. |  |  |  |  |  |  |  |
|  |  | Freq.: ______. |  |  |  |  |  |  |  |
|  |  | Phase/Wire:________. |  |  |  |  |  |  |  |
|  |  | Power Factor: ______. |  |  |  |  |  |  |  |
|  |  | Voltage Output: ________. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify generator circuit breaker settings. | Circuit breaker size and phase: ____________. |  |  | Record results in Data Table. Ground fault indication and alarm is recommended |  |  |  |  |
|  |  | Ground fault protection is disabled. |  |  |  |  |  |  |  |
|  |  | Circuit breaker is set per the coordination study. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Inspect physical and mechanical condition. | No visible damage to generator or enclosure. |  |  |  |  |  |  |  |
|  |  | Engine generator exterior is clean and dry. |  |  |  |  |  |  |  |
|  |  | Generator control panel interior is clean and dry. |  |  |  |  |  |  |  |
|  |  | Generator control panel mounted at an accessible height. |  |  |  |  |  |  |  |
|  |  | Vibration isolation is installed at engine and at radiator. |  |  |  |  |  |  |  |
|  |  | All external connections are made with flexible connections. |  |  |  |  |  |  |  |
|  |  | Verify remote monitoring wiring is connected and labeled. |  |  |  |  |  |  |  |
|  |  | Verify control wiring is connected and labeled. |  |  |  |  |  |  |  |
|  |  | Feeder cable/bus routing doesn’t obstruct access for operation or maintenance. |  |  |  |  |  |  |  |
|  |  | Control wiring harness(es) does not rub against vibrating or moving parts. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify anchoring | Anchor bolts are provided in locations shown on manufacturer's drawings. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify equipment grounding | Verify ground rod is installed with connection to engine generator frame. |  |  |  |  |  |  |  |
|  |  | Generator neutral bonded to ground with conductor sized per NEC 250-20. |  |  |  |  |  |  |  |
|  |  | Measured diameter of bare copper conductor corresponds to diameter of specified conductors. |  |  |  |  |  |  |  |
|  |  | Ground strap from engine to frame. |  |  |  |  |  |  |  |
|  |  | Ground strap from generator enclosure to frame. |  |  |  |  |  |  |  |
|  |  | Ground bus provided in termination cabinet with properly terminated ground conductors. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify lube oil levels are within manufacturer’s recommended limits | Lube oil level is filled to proper level. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify fuel system installation and integrity | Day tank is full of fuel (90% for diesel). |  |  |  |  |  |  |  |
|  |  | Fuel level in day tank matches fuel gauge. |  |  |  |  |  |  |  |
|  |  | Remote fueling station is installed and operating properly. |  |  |  |  |  |  |  |
|  |  | There are not clearance issues with the remote fueling station. |  |  |  |  |  |  |  |
|  |  | All alarms are operating properly from remote fueling station to Building Automation System (BAS). |  |  |  |  |  |  |  |
|  |  | Fuel system is free of leaks. |  |  |  |  |  |  |  |
|  |  | Flexible fuel lines are installed at engine. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify cooling system installation and integrity | Coolant level is filled to proper level. |  |  | Record radiator name plate date in data table. |  |  |  |  |
|  |  | Verify coolant system freeze protection level. |  |  |  |  |  |  |  |
|  |  | Cooling system is free from leaks. |  |  |  |  |  |  |  |
|  |  | Flexible coolant lines are installed between engine and radiator. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify exhaust system installation and integrity | Exhaust system, silencer and flexible connector installed and supported. |  |  |  |  |  |  |  |
|  |  | Exhaust system expansion is not transferred to engine components such as turbocharger. |  |  |  |  |  |  |  |
|  |  | Silencer is equipped with condensate drain plug and turn valve. |  |  |  |  |  |  |  |
|  |  | Exhaust system is equipped with rain cap. |  |  |  |  |  |  |  |
|  |  | Exhaust system is properly insulated within building. |  |  |  |  |  |  |  |
|  |  | Exhaust system has at least 9” clearance from combustible materials. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| ELECTRICAL INTEGRITY |  |  |  |  |  |  |  |  |  |
|  | Verify operation of coolant line heater. | Verify that valves to the water jacket heater are open. |  |  | Record results in Data Table. Record supply voltages and amperage with heaters and pump in operation. Calculate heater and pump wattage based on line voltage and current. Verify wattage calculated is same as shop drawing data. Manufacturer’s Specifications: Heater: Watts _____ Volts ______ Phase _____ Pump: Watts _____ Volts ______ Phase _____ |  |  |  |  |
|  |  | Verify thermostats switch at their setpoint temperatures (110°F). |  |  |  |  |  |  |  |
|  |  | Verify pump runs continuously independent of heater operation. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify operation of battery and starting system. | Loss of Power Alarm is operable. |  |  | Record results in Data Table. Record cell voltages for all cells with terminals available, total battery charging voltage and charging current. Manufacturer’s Specifications: Nom. Batt. Voltage: __________ Rec. Float Charge Voltage: ________ Float Voltage: _______ Equalize Voltage: _____ Max over float Ampere Taper (Max to Min): ______ Nominal Output Voltage: ______ Input Voltage: _______ Ambient Temp: -40ºF to 122ºF |  |  |  |  |
|  |  | Low Battery Volt Alarms at: 18.6V-25.7V. |  |  |  |  |  |  |  |
|  |  | High Battery Volt Alarms at: 26.9V-36.3V. |  |  |  |  |  |  |  |
|  |  | Power On led in on. |  |  |  |  |  |  |  |
|  |  | Battery Heater Pad: 120VAC input. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify operation of generator space heaters | Space heaters operate when generator is not running and not operating while generator is running. |  |  | Record results in Data Table. Record supply voltages and amperage with heater in operation. Calculate heater wattage based on line voltage and current. Verify wattage calculated is same as shop drawing data. Manufacturer’s Specifications: Heater: Watts _____ Volts ______ Phase _____ |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Perform an insulation resistance test at 1000 VDC on generator windings. | Minimum insulation resistance value is 100 Megohoms. |  |  | Record results in Data Table. Take reading at 1 minute. Take reading at 10 minutes. Record ambient temperature and relative humidity. Test Name: Insulation Resistance. Reference Equip. Table |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | With the breaker in the closed position, measure the contact resistance of each phase of the primary circuit. | Readings are within 50% of the lowest value. |  |  | Record results in Data Table. Test Name: Contact Resistance Reference Equip. Table |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Perform an insulation resistance test on the Generator Circuit Breaker at 1000VDC, phase-to-phase and phase to ground, connected to the bus in the closed position, in accordance with NETA Table 100.1. | Minimum insulation resistance shall be 100 Megohms. |  |  | Record results in Data Table. Test for one minute in accordance with NETA Table 100.1. Test Name: Insulation Resistance Reference Equip. Table |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Test the Long Time Delay (LTD) (seconds) and Long Time Pickup current (LDPU) (amperes) setting of the breaker, by using primary current injection. | Long delay current pick up and time delay per coordination study. |  |  | Record results in Data Table. Test Name: Primary Current Inject. Reference Equip. Table |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Test the Short Time Delay (STD) (seconds) and Short Time Pickup current (SDPU) (amperes) setting of the breaker, by using primary current injection. | Short delay current pick up and time delay per coordination study. |  |  | Record results in Data Table. Test Name: Primary Current Inject. Reference Equip. Table |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Test the Instantaneous Time Delay (ITD) (seconds) and Instantaneous Time Pickup current (INSTPU) (amperes) setting of the breaker, by using primary current injection. | Instantaneous pick up per coordination study. |  |  | Record results in Data Table. Test Name: Primary Current Inject. Reference Equip. Table |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Test the Ground Fault Delay (GFD) (seconds) and Ground Fault Pickup current (GFPU) (amperes) setting of the breaker, by using primary current injection. | Instantaneous pick up per coordination study. |  |  | Record results in Data Table. Test Name: Primary Current Inject. Reference Equip. Table |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| ALARMS AND CONTROL PANEL TEST |  |  |  |  |  |  |  |  |  |
|  | Verify control wiring between generator and ATS are correctly terminated. | Terminations match shop drawings. |  |  | Note: this step applies to field land terminations only |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Record all setpoints at Engine Generator Control Panel. |  |  |  | Manufacturer’s checklist can be attached to this form in lieu of recording |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify all warning/pre-alarms per manufacturer’s instructions and verify operation and local annunciation at Engine Generator Control Panel. | Overcrank. |  |  | 1-13 NFPA 110 Spec Section 16231 |  |  |  |  |
|  |  | Low Water Temp. |  |  |  |  |  |  |  |
|  |  | High Water Temp. |  |  |  |  |  |  |  |
|  |  | Low Oil Pressure. |  |  |  |  |  |  |  |
|  |  | Overspeed. |  |  |  |  |  |  |  |
|  |  | Low Coolant Level. |  |  |  |  |  |  |  |
|  |  | EPS Supplying Load. |  |  |  |  |  |  |  |
|  |  | Control switch not in Auto. |  |  |  |  |  |  |  |
|  |  | High Battery Voltage. |  |  |  |  |  |  |  |
|  |  | Low Battery Voltage. |  |  |  |  |  |  |  |
|  |  | Battery Charger AC Failure. |  |  |  |  |  |  |  |
|  |  | Lamp Test. |  |  |  |  |  |  |  |
|  |  | Contacts for local and remote common alarm. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify all shutdown conditions per manufacturer’s instructions and verify operation and local annunciation at Engine Generator Control Panel. | Overcrank. |  |  | 1-5 NFPA 110 Spec Section 16231 |  |  |  |  |
|  |  | High Water Temp. |  |  |  |  |  |  |  |
|  |  | Low Oil Pressure. |  |  |  |  |  |  |  |
|  |  | Overspeed. |  |  |  |  |  |  |  |
|  |  | Low Coolant Level. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify remote audible annunciation of all status, warning/pre-alarm, and shutdown conditions per manufacturer’s instructions. | Overcrank. |  |  | 1-9 NFPA 110 Spec Section 16231 |  |  |  |  |
|  |  | Low Water Temp. |  |  |  |  |  |  |  |
|  |  | High Water Temp. |  |  |  |  |  |  |  |
|  |  | Low Oil Pressure. |  |  |  |  |  |  |  |
|  |  | Overspeed. |  |  |  |  |  |  |  |
|  |  | Low Coolant Level. |  |  |  |  |  |  |  |
|  |  | Control switch not in Auto. |  |  |  |  |  |  |  |
|  |  | Contacts for local and remote common alarm. |  |  |  |  |  |  |  |
|  |  | Audible alarm silencing switch. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify installation of remote E-Stop | Located outside of generator room door. Near each exit/entrance to genset room. Located locally on the genset package. |  |  |  |  |  |  |  |
|  |  | Cover not damaged, scratched, or broken. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Verify remote annunciation of engine conditions at building automation system | Annunciator panel lights & alarms function by initiating test switch. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | With generator in a “cold start” condition, conduct a load performance test, by initiating a NORMAL failure and transfer of ATS’s for time specified in the remarks column. | Engine starts and runs. |  |  | Record results in Data Table. Load generator for a maximum of 2 hrs using available building load and/or a load bank During test, verify exhaust, coolant, and fuel system is functioning properly. Test Name: 2 Hour Load Bank Test Reference Equip. Table |  |  |  |  |
|  |  | Air intake louvers open fully. |  |  |  |  |  |  |  |
|  |  | Exhaust damper opens fully. |  |  |  |  |  |  |  |
|  |  | Fuel is not leaking. |  |  |  |  |  |  |  |
|  |  | Coolant is not leaking. |  |  |  |  |  |  |  |
|  |  | Lube oil is not leaking. |  |  |  |  |  |  |  |
|  |  | Exhaust system expansion is not transferred to engine system components. |  |  |  |  |  |  |  |
|  |  | Exhaust system is not leaking. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Restore normal sources to ATS’s (or turn off load bank) and transfer ALL load off of generator and allow to cool down for 5 minutes | Generator runs in cool down mode for 5 min. |  |  | Test Name: 2 Hour Load Bank Test Reference Equip. Table |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Disconnect emergency feeders to ATS and connect load bank directly to load side of generator |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | With a load bank connected to the load side terminals of the generator, start generator at local control panel with engine control switch | Engine starts and runs. |  |  | Test Name: 4 Hour Load Bank Test Reference Equip. Table |  |  |  |  |
|  |  | Air intake louvers open fully. |  |  |  |  |  |  |  |
|  |  | Exhaust damper opens fully. |  |  |  |  |  |  |  |
|  |  | Fuel is not leaking. |  |  |  |  |  |  |  |
|  |  | Coolant is not leaking. |  |  |  |  |  |  |  |
|  |  | Lube oil is not leaking. |  |  |  |  |  |  |  |
|  |  | Exhaust system expansion is not transferred to engine system components. |  |  |  |  |  |  |  |
|  |  | Exhaust system is not leaking. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Conduct a load performance test utilizing a load bank to achieve 100% rated load of generator for time specified in the remarks column. |  |  |  | Record results in Data Table. Load generator at 50% for 15 min. Load generator at 75% for 15 min. Load generator at 100% for 3.5 hrs During test, verify exhaust, coolant, and fuel system is functioning properly. Test Name: 4 Hour Load Bank Test Reference Equip. Table |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | In conjunction with load performance test, verify voltage regulation by recording RMS voltage while increasing load on generator. | Voltage regulation is ±1%. |  |  | Record results in Data Table Record voltage at no load. Record voltage at 50% load. Record voltage at 75% load. Record voltage at 100% load. Calculate voltage regulation percentage. Test Name: Volt. & Freq. Regulation Reference Equip. Table |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | In conjunction with load performance test, verify frequency regulation by recording frequency while increasing load on generator. | Frequency regulation is ±1% |  |  | Record results in Data Table Record frequency at no load. Record frequency at 50% load. Record frequency at 75% load. Record frequency at 100% load. Calculate voltage regulation percentage. Test Name: Volt. & Freq. Regulation Reference Equip. Table |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | During load performance test, verify engine operation is within normal operating limits. |  |  |  | Manufacturer’s Specifications: RPM @ 60Hz: 1800 RPM Coolant Amb. Temp: 190ºF |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | During load performance test, verify correct phase rotation. | Phase rotation at generator matches NORMAL power source. |  |  | A(U), B(V), C(W) Test Name: Phase Rotation Reference Equip. Table |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | During step 3, while generator is running at 100% load, measure sound level. | Measured sound pressure level in rooms directly adjoining the generator room, as well as above and below, if applicable. |  |  | Record results in Data Table. Test Name: Sound Level Reference Equip. Table |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | While generator is running at 100% load, conduct Exhaust-System Back Pressure Test | Maximum backpressure at full-rated load is within manufacturer’s written maximum allowable limits of 6.7 kPa or 26.9” H20 for the engine. |  |  | Record results in Data Table. Connect test instrumentation to exhaust line close to engine exhaust manifold. Test Name: Back Pressure Test Reference Equip. Table |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Decrease load to 0% and allow the generator to cool down for 5 minutes | Generator cools down. |  |  | Test Name: 4 Hour Load Bank Test |  |  |  |  |
|  |  | No leaks from any system are found. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | After the cool down, once the prime mover has reached rated voltage and frequency, transfer full rated load onto the engine generator in a single block. | Engine continues to run without shutdown or overspeed trip and recovers to steady state voltage and frequency ranges within 5 seconds. |  |  | Test Name: Block Load Test |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Decrease load to 0% and shutdown generator with local E-Stop. | Generator shuts down. |  |  |  |  |  |  |  |
|  |  | Remote annunciator alarms with E-Stop. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Disconnect fuel solenoid and simulate start to engine. | Engine cycle cranks a minimum of three 15-second cranking cycles with 15 seconds between cycles. |  |  |  |  |  |  |  |
|  |  | At completion of third cycle engine stops cranking and “overcrank” shutdown alarm is annunciated locally and remotely. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
| FINAL INSPECTION |  |  |  |  |  |  |  |  |  |
|  | After testing is performed on the generator, verify tightness of field landed feeder terminations. | Primary feeder cable connections properly torqued and marked. |  |  | Record results in Data Table. Bolted torque should comply with NETA Table 100.12 unless manufacturer specified values are listed on the equipment. Secondary distribution feeder connections are not included in the test. Test Name: Bolt Torque Reference Equip. Table |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |
|  | Refill fuel tanks and verify 90% fuel levels | Fuel level indicator verifies 90% fuel level in day tank. |  |  |  |  |  |  |  |
|  |  | Fuel level indicator verifies 90% fuel level in storage tank. |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |

## NAMEPLATE DATA

### Engine Nameplate (May be found in multiple nameplate locations)

| Parameter | Data |
| --- | --- |
| Equipment ID |  |
| Manufacturer |  |
| Serial Number |  |
| Model Number |  |
| Date Manufactured |  |
| Horsepower |  |
| kW |  |

## Generator Nameplate

| Parameter | Data |
| --- | --- |
| Manufacturer |  |
| Serial Number |  |
| Model Number |  |
| Date Manufactured |  |
| Volts |  |
| Amps |  |
| KVA |  |
| Frequency |  |
| RPM |  |
| KW |  |
| PF |  |
| Insulation Class: |  |

## Battery Nameplate

| Parameter | Data |
| --- | --- |
| Manufacturer |  |
| Serial Number |  |
| Model Number |  |
| Quantity |  |
| Volts |  |
| Cold Cranking Amps |  |

## Battery Charger Nameplate

| Parameter | Data |
| --- | --- |
| Manufacturer |  |
| Serial Number |  |
| Model Number |  |
| Input Amps |  |
| Input Volts |  |
| Output Amps |  |
| Output Volts |  |

Circuit Breaker Name Plate Data

| Parameter | Data |
| --- | --- |
| Manufacturer: |  |
| Type/Model: |  |
| Serial Number: |  |
| Frame Size/Rating |  |
| Interrupting Rating |  |
| Voltage Rating |  |

Radiator Nameplate

| Parameter | Data |
| --- | --- |
| Manufacturer |  |
| Serial Number |  |
| Model Number |  |
| Date Manufactured |  |

Coolant Pump(s) & Heater(s)

| Designation | Volts | Amps | Watts |
| --- | --- | --- | --- |

Battery System

| Cell Volts | Charging Volts | Charging Amps |
| --- | --- | --- |

Space Heater(s)

| Designation | Voltage | Amperage | Wattage |
| --- | --- | --- | --- |

## Test Equipment Used:

| Test Name | Manufacturer | Model Number | Serial Number | Calibration(Date) |
| --- | --- | --- | --- | --- |

Insulation Resistance (1000 VDC)

| Generator Windings | A-B | B-C | C-A | A-G | B-G | C-G |
| --- | --- | --- | --- | --- | --- | --- |
| 1 Minute (Meg Ohms) |  |  |  |  |  |  |
| 10 Minutes (Meg Ohms) |  |  |  |  |  |  |
| Circuit Breaker |  |  |  |  |  |  |
| 1 Minute (Meg Ohms) |  |  |  |  |  |  |

Circuit Breaker Contact Resistance

| Phase | A | B | C |
| --- | --- | --- | --- |
| (Micro Ohms) |  |  |  |

Current Injection

| Function | Actual Set. | Test Setting | Test Point | Nominal Val. | A | B | C |
| --- | --- | --- | --- | --- | --- | --- | --- |
| LTD |  |  |  |  |  |  |  |
| LDPU |  |  |  |  |  |  |  |
| STD |  |  |  |  |  |  |  |
| SDPU |  |  |  |  |  |  |  |
| INSTPU |  |  |  |  |  |  |  |
| GFD |  |  |  |  |  |  |  |
| GFPU |  |  |  |  |  |  |  |

2 Hour Load Bank Test

| Crank Time Until Prime Mover Start and Runs |  |
| --- | --- |
| Time Required for Prime Mover to Come Up to Operating Speed |  |
| Voltage Overshoot |  |
| Frequency Overshoot |  |
| Time Required to Achieve Steady State Operation |  |

| Time |  | Load | RPM | Freq. | Amps | Volts | kW | Oil Press | Oil Temp | Exhaust Temp | Cool. Temp | Fuel Level | Batt. Chrg Rate |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 5 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 10 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 15 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 30 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 45 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 1 hour |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 1 hour 15 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 1 hour 30 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 1 hour 45 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 2 hour |  | 100% |  |  |  |  |  |  |  |  |  |  |  |

4 Hour Load Bank Test

| Time |  | Load | RPM | Freq. | Amps | Volts | kW | Oil Press | Oil Temp | Exhaust Temp | Cool. Temp | Fuel Level | Batt. Chrg Rate |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0 min |  | 50% |  |  |  |  |  |  |  |  |  |  |  |
| 5 min |  | 50% |  |  |  |  |  |  |  |  |  |  |  |
| 10 min |  | 50% |  |  |  |  |  |  |  |  |  |  |  |
| 15 min |  | 75% |  |  |  |  |  |  |  |  |  |  |  |
| 30 min |  | 75% |  |  |  |  |  |  |  |  |  |  |  |
| 45 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 1 hour |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 1 hour 15 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 1 hour 30 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 1 hour 45 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 2 hour |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 2 hour 15 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 2 hour 30 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 2 hour 45 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 3 hour |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 3 hour 15 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 3 hour 30 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 3 hour 45 min |  | 100% |  |  |  |  |  |  |  |  |  |  |  |
| 4 hour |  | 100% |  |  |  |  |  |  |  |  |  |  |  |

Voltage & Frequency Regulation

| Function | 50% Load | 75% Load | 100% Load |
| --- | --- | --- | --- |
| Voltage (V) |  |  |  |
| Frequency (hz) |  |  |  |

Phase Rotation – (Circle Phase Rotation)

| Normal Power | A B C | A C B |
| --- | --- | --- |
| Emergency Power | A B C | A C B |

Sound Level

| Location | Decibel (DB) |
| --- | --- |

Back Pressure Test

| System Exhaust Pressure | Location |
| --- | --- |

Block Load Test

Recovery Time:   _________

Bolt Torque (Newton Meters or Foot Pounds)

| Bolt/Lug | A | B | C | N | G |
| --- | --- | --- | --- | --- | --- |
| Normal |  |  |  |  |  |
| Emergency Lugs |  |  |  |  |  |

| ## Final Sign-Off |  |  |  |  |
| --- | --- | --- | --- | --- |
| Commissioning Agent | Printed Name | Initials | Date |  |
| CONTRACTOR | PRINTED NAME | INITIALS | DATE |  |
| General Contractor (GC) |  |  |  |  |
| Mechanical Contractor (MC) |  |  |  |  |
| Electrical Contractor (EC) |  |  |  |  |
| TAB Contractor (TAB) |  |  |  |  |
| Controls Contractor (CC) |  |  |  |  |
| Owner’s O&M Personnel |  |  |  |  |