# Automatic Transfer Switches

# Functional Performance Test

| Equipment ID | [Equipment ID] |
| --- | --- |
| Building | [Building] |
| Location | [Room] |

## System Description

Description:

Operational Assumptions:

| Initial Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 1 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Re-Test 2 |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

| Deferred/Seasonal Test |  | Start Date | End Date | Initials |
| --- | --- | --- | --- | --- |
| Results (Check one) | Explanation: |  |  |  |
| Pass Fail Partial Test w/Corrective Actions Complete Test w/Corrective Actions Other |  |  |  |  |

## Test Participants

| Organization | Required | Optional |
| --- | --- | --- |
| General Contractor |  |  |
| Mechanical Contractor |  |  |
| Electrical Contractor |  |  |
| TAB Contractor |  |  |
| Controls Contractor |  |  |
| Owner’s O&M Personnel |  |  |

## Test Equipment Required (to be provided by the Contractor

| Test Name | Equipment Description |
| --- | --- |
| Bolt Torque | Calibrated torque wrench |
| Bolted Connection or Contact Resistance | Four-probe Digital Low Resistance Ohmmeter (DLRO) |
| Voltage/Continuity | DVM |
| Insulation Resistance | Battery or line-powered (Hand-crank not acceptable). |
| Relay Operation | Variable AC Voltage source |

## System Readiness Summary Checklist

| Description | Yes | No | Date |
| --- | --- | --- | --- |
| System Ready for Test |  |  |  |
| Required Personnel Available |  |  |  |
| Required Tools/Test Equipment/Supplies Available |  |  |  |
| Required Safety Equipment Available |  |  |  |

## Functional Performance Test -- (Verify all components are ready before energizing or operating the system.)

The Commissioning Authority will make and document any changes/addition/deletions to this test procedure required by current system conditions (i.e. weather, system load, utility availability, etc.).

R = Retest (Check () retest required)								Y= Checked and Passed

C = Corrected (Check () when correction verified)					              N = Not Passed

| ACTION |  | REQUIRED REACTION | Y () | N () | COMMENTS |  | R () |  | C () |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| PRE-TEST VISUAL MECHANICAL INSPECTION |  |  |  |  |  |  |  |  |  |  |
|  | Safe conditions (protective gear in-place, available & procedures observed) |  |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Confirm that NORMAL and EMERGENCY sources match final design drawings. | Normal: MDS. |  |  | Source: Normal: ________ Emergency: ________ |  |  |  |  |  |
|  |  | Emergency: EDP. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Verify equipment nameplate data matches one-line drawings, specifications, and/or shop drawings and record date on attached table. | Volts:________. |  |  |  |  |  |  |  |  |
|  |  | Amps:________. |  |  |  |  |  |  |  |  |
|  |  | 4 pole, 4W. |  |  |  |  |  |  |  |  |
|  |  | Frequency: 60hZ. |  |  |  |  |  |  |  |  |
|  |  | Interrupting Rating:______. |  |  |  |  |  |  |  |  |
|  |  | Enclosure:______. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Verify permanent labels for transfer switch is installed. | Melamine plastic laminate, minimum 1/16” thick. |  |  | Spec Section 16075 |  |  |  |  |  |
|  |  | Black letters on white face. |  |  |  |  |  |  |  |  |
|  |  | Secured with self tapping, stainless-steel (SS) screws or SS machine screws with nuts and flat and lock washers. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Verify accessibility for maintenance. | Door opens freely and swings fully open. |  |  |  |  |  |  |  |  |
|  |  | 3’-6” minimum clearance in front of switch. |  |  |  |  |  |  |  |  |
|  |  | Cables do not block access to indicators or adjustable components. |  |  |  |  |  |  |  |  |
|  |  | Cables do not block access to manual transfer switch operator. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Inspect physical and mechanical conditions. | No visible signs of damage. |  |  |  |  |  |  |  |  |
|  |  | No visible dirt, metal chips or contamination. |  |  |  |  |  |  |  |  |
|  |  | Appropriate source indicating lights are illuminated. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Verify anchoring. | Anchor bolts are provided in locations shown on manufacturer's drawings. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Verify the barriers and arc chutes are properly installed around contacts. | Barriers partially surround ATS contacts and are insulated. |  |  |  |  |  |  |  |  |
|  |  | Arc chutes are installed around the contacts. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Verify ATS is properly grounded. | Enclosure bonded to ground bus. |  |  |  |  |  |  |  |  |
|  |  | Incoming (normal and emergency) and outgoing (load) feeder grounding conductors bonded to ground bus. |  |  |  |  |  |  |  |  |
|  |  | Neutral bus/pole isolated from ground. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Confirm that components of control system including terminal block, wiring, and Ni-Cad batteries are complete. |  |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Perform manual transfer operation with both NORMAL and EMERGENCY sources de-energized. Use detachable manual operator to transfer from NORMAL to EMERGENCY and back. | Switch should transfer smoothly and with full contact travel speed. |  |  |  |  |  |  |  |  |
|  |  | Mechanical interlocking should prevent simultaneous closure of NORMAL and EMERGENCY sources. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Perform manual bypass operation to each source. | Switch should transfer smoothly and with full contact travel speed. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| ELECTRICAL INTEGRITY |  |  |  |  |  |  |  |  |  |  |
|  | Measure contact resistance on all poles in both closed positions. | Readings are within 50% of the average value, including the neutral pole. |  |  | Record results in Data Table. Spec Section 16415 |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Perform an insulation resistance test at 1000VDC on each bus section, phase-to-phase and phase to ground. | Minimum insulation resistance shall be 100 megohms. |  |  | Record results in Data Table. Test for one minute in accordance with NETA Table 100.1. Isolate ALL control wiring and electronic devices prior to testing. Test across open contacts for both NORMAL and EMERGENCY sources. Test phase-to-ground with all other phases grounded for both NORMAL and EMERGENCY sources. Spec Section 16415 Test Name: Insulation Resistance, Reference Equipment Table |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Perform insulation resistance test at 1000 VDC to verify Automatic Transfer Switch is isolated from load when bypassed. | Insulation resistance shall equal or exceed 100 Megohms. |  |  | Record results in Data Table. Test for one minute in accordance with NETA Table 100.1. Isolate ALL control wiring and electronic devices prior to testing Test Name: Insulation Resistance, Reference Equipment Table |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Verify the operation of four-line LCD display and character keyboard. | All data displays operate. |  |  | Record Password: _______ |  |  |  |  |  |
|  |  | All program parameters accessible. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Verify “In Phase Monitoring” setting. | In phase monitoring is enabled. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Verify all voltage, frequency, and time delay settings. | Use ATS microprocessor control system. |  |  | Record values in the “Actual Setpoint” column in the ATS Parameters and Setpoints table Spec Section 16415 |  |  |  |  |  |
|  |  | Device pick-up (PU) and drop-out (DO). |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Verify all applicable local and remote annunciation by the monitoring system for various operating conditions. | Operating Conditions: NORMAL power available |  |  |  |  |  |  |  |  |
|  |  | EMERGENCY power avail. |  |  |  |  |  |  |  |  |
|  |  | ATS in NORMAL position. |  |  |  |  |  |  |  |  |
|  |  | ATS in EMERGENCY position. |  |  |  |  |  |  |  |  |
|  |  | LED indicating lights are operating. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Verify proper phase rotation | Emergency source matches utility source. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| TRANSFER OPERATION TESTS |  |  |  |  |  |  |  |  |  |  |
|  | Disconnect NORMAL power source to transfer switch. | Time delay on engine start equals setpoint. |  |  | Record results in Data Table. Spec Section 16231 |  |  |  |  |  |
|  |  | Start signal sent to engine generator. |  |  |  |  |  |  |  |  |
|  |  | Transfer time delay equals setpoint. |  |  |  |  |  |  |  |  |
|  |  | Time delay in neutral equals setpoint. |  |  |  |  |  |  |  |  |
|  |  | ATS transfers to Emergency source position. |  |  |  |  |  |  |  |  |
|  |  | Total time to connect to Emergency source is no more than 10-seconds. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Restore Normal power source to Automatic Transfer Switch to verify setpoints. | Re-transfer time delay equals setpoint. |  |  | Record results in Data Table. Spec Section 16231 |  |  |  |  |  |
|  |  | ATS transfers to Normal source position. |  |  |  |  |  |  |  |  |
|  |  | Time delay in neutral equal setpoint. |  |  |  |  |  |  |  |  |
|  |  | Engine cool down time delay equals setpoint. |  |  |  |  |  |  |  |  |
|  |  | Engine shuts off after cool down delay times out. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Repeat steps #21 and #22, except manually disconnect. EMERGENCY source, to simulate failure of the engine, after restoration of NORMAL power and before the re-transfer delay has expired. | Switch should re-transfer to Normal without delay on engine shutdown. |  |  | Spec Section 16231 |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Verify operation of ATS TEST switch. | Simulates failure of normal source. |  |  | Spec Section 16231 |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| BYPASS AND ISOLATION SWITCH OPERATION |  |  |  |  |  |  |  |  |  |  |
|  | Verify Automatic Transfer Switch manual bypass and isolation switch operation with NORMAL source energized and load on ATS. | ATS mechanism is de-energized and power passes through the bypass/isolation switch path. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Restore the Automatic Transfer Switch to its automatic mode by manually reversing the bypass and isolation switch operation. | ATS mechanism is energized and the bypass/isolation switch path is de-energized. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
| FINAL INSPECTION |  |  |  |  |  |  |  |  |  |  |
|  | After testing is performed on the ATS, verify tightness of field landed feeder terminations (NORMAL, EMERGENCY, and LOAD feeders). | Feeder cable connections properly torqued and marked. |  |  | Record results in Data Table. Bolted torque should comply with NETA Table 100.12 unless manufacturer specified values are listed on the equipment. Test Name: Bolt Torque Reference Equip. Table |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |
|  | Prior to energization, inspect interior hardware. | All hardware in place and properly torqued. |  |  |  |  |  |  |  |  |
|  |  | Compartments clear of tools and hardware. |  |  |  |  |  |  |  |  |
| Record issues |  |  |  |  | Issue Log Item: |  |  |  |  |  |
|  |  |  |  |  | Initial | Date |  |  |  |  |

### Test Equipment Used:

| Test Name | Manufacturer | Model Number | Serial Number | Calibration(Date) |
| --- | --- | --- | --- | --- |

### ATS NAMEPLATE DATA

| Parameter | Data |
| --- | --- |
| Equipment ID |  |
| Manufacturer |  |
| Model |  |
| Serial No. |  |
| Catalog No |  |
| Mfg. Date |  |
| Current Rating |  |
| Voltage Rating |  |
| Poles: |  |
| Closing & Withstand Amps |  |
| NEMA Enclosure |  |

### Contact Resistance

| Contacts | A | B | C | N |
| --- | --- | --- | --- | --- |
| Normal |  |  |  |  |
| Emergency |  |  |  |  |

### Insulation Resistance

| Phase to Phase | A – B | B - C | C – A |
| --- | --- | --- | --- |
| Normal |  |  |  |
| Emergency |  |  |  |
| Phase to Ground | A - G | B - G | C – G |
| Normal |  |  |  |
| Emergency |  |  |  |
| To Load (ATS in Bypass) | A – LOAD | B – LOAD | C - LOAD |
| Normal |  |  |  |
| Emergency |  |  |  |

### PARAMETERS AND SETPOINTS

### Voltage

| Parameter | Actual Setpoint | Specification Setpoint | Range | Factory Default |
| --- | --- | --- | --- | --- |
| Normal Over-Voltage Dropout |  |  |  |  |
| Normal Over -Voltage Pickup |  |  |  |  |
| Emergency Over-Voltage Dropout |  |  |  |  |
| Emergency Over -Voltage Pickup |  |  |  |  |
| Normal Under-Voltage Dropout |  |  |  |  |
| Normal Under-Voltage Pickup |  |  |  |  |
| Emergency Under-Voltage Dropout |  |  |  |  |
| Emergency Under-Voltage Pickup |  |  |  |  |

### Frequency

| Parameter | Actual Setpoint | Specification Setpoint | Range | Factory Default |
| --- | --- | --- | --- | --- |
| Normal Over-Frequency Dropout |  |  |  |  |
| Normal Over -Frequency Pickup |  |  |  |  |
| Emergency Over-Frequency Dropout |  |  |  |  |
| Emergency Over -Frequency Pickup |  |  |  |  |
| Normal Under-Frequency Dropout |  |  |  |  |
| Normal Under-Frequency Pickup |  |  |  |  |
| Emergency Under-Frequency Dropout |  |  |  |  |
| Emergency Under-Frequency Pickup |  |  |  |  |

### Time Delay

| Parameter | Actual Setpoint | Specification Setpoint | Range | Factory Default |
| --- | --- | --- | --- | --- |
| Neutral Position Time Delay |  |  |  |  |
| Normal Failure Time Delay (Gen Start) |  |  |  |  |
| Emergency Failure Time Delay |  |  |  |  |
| Transfer to Emergency Time Delay |  |  |  |  |
| Return to Normal Time Delay |  |  |  |  |
| Engine Cool Down |  |  |  |  |

Note:  The “Actual Setpoint” column in the above table should be filled in during step 0

### Feeder Termination Torque  (Newton Meters or Foot-Pounds)

| ### TORQUE FEEDERS | ### A | ### B | ### C | ### N | ### G |
| --- | --- | --- | --- | --- | --- |
| ### NORMAL |  |  |  |  |  |
| ### EMERGENCY |  |  |  |  |  |
| ### LOAD |  |  |  |  |  |

| ## Final Sign-Off |  |  |  |  |
| --- | --- | --- | --- | --- |
| Commissioning Agent | Printed Name | Initials | Date |  |
| CONTRACTOR | PRINTED NAME | INITIALS | DATE |  |
| General Contractor (GC) |  |  |  |  |
| Mechanical Contractor (MC) |  |  |  |  |
| Electrical Contractor (EC) |  |  |  |  |
| TAB Contractor (TAB) |  |  |  |  |
| Controls Contractor (CC) |  |  |  |  |
| Owner’s O&M Personnel |  |  |  |  |