## Exterior & Interior
Appendix A Security Door Opening Matrix Department of Veterans Affairs
The matrix below is organized alphabetically by building or facility type. Within each building or facility type, the security door openings are separated into exterior and interior (highlighted in blue) locations and are also listed alphabetically within each of those categories. | [20 empty] | 2015-01-01
|  |  | Door Types | SDO Hardware | Facility Classification | Access Control | [9 empty] | Monitoring |  |  |  | Notes
Facility Type/Door Location | [5 empty] | Card Reader | Fail Safe | Fail Secure | Key Storage Box | ANSI/BMHA Function | Magnetic Lock | Electric Strike | Request to Exit PIR | Exit Button or Crashbar Integrated to Lock | PIN or Biometrics | Door Contact | IDS with Audible and Remote Alarm | PIN or Biometrics | Force or Hold-open Alarm
Ambulatory Care Clinic/Outpatient Clinic
Egress |  |  | A, C | 104 | New/Exist |  |  |  |  | F01 Exit | [5 empty] | X | X |  |  | 2
Emergency Access |  |  | A | 110 | New/Exist |  |  |  | X | F07 Store-room
Guard House at Site Perimeter |  |  | A, B | 114 | New/Exist |  |  |  | X | F07 Store-room | [9 empty] | 9
Loading Dock (Overhead) |  |  | Overhead | 108 | New/Exist | X | [9 empty] | X
Loading Dock (Swinging) |  |  | A, C | 107 | New | X |  | X | X | F07 Store-room |  | X |  |  |  | X |  |  | X | 18
Loading Dock (Swinging) |  |  | A, C | 107 | Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X
Public Entrances |  |  | A, B, C, D | 101 | New/Exist | X | X |  |  |  | X | X | X | X |  | X |  |  |  | 1
Roof Access |  |  | A, C | 116 | New/Exist |  |  |  | X | F07 Store-room | [5 empty] | X
Roof Hatch |  |  | Not Applic. | 115 | New/Exist |  |  |  | X | [6 empty] | X |  |  |  | 17
Staff |  |  | A, B, C, D | 103 | New/Exist | X | X |  |  | F04 Entry | X | X | X | X |  | X |  |  |  | 2, 3, 4
Storage (non-pilferable items) |  |  | A, C | 109 | New/Exist |  |  |  | X | F07 Store-room | [9 empty] | 7, 8
Storage (pilferable items) |  |  | A, C | 109 | New/Exist | X |  |  | X | F07 Store-room |  | X | X |  |  | X |  |  | X | 7, 8
Tunnel |  |  | A | 111 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X |  |  | 8
Utility Connections (Commercial Power and Med Gas Stor) |  |  | A, C | 111 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X |  |  | 8
Utility Connections (Demarc Room) |  |  | A, C | 113 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X |  |  |  | 8
Building Systems Room from Corridor |  |  | A, C | 228 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  | X | 8, 18
Central Linen Storage and Distribution from Corridor |  |  | A, C | 215 | New/Exist | X | X | [8 empty] | X |  |  | X
Elevator Equipment Room from Corridor |  |  | A, C | 228 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  | X | 8,18
Evidence Storage from Corridor |  |  | A | 220 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  | X | 13, 18
Fire Control Center to Building Interior |  |  | A | 224 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X |  |  | 8
Holding Area |  |  | A | 205 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  | X | 10, 18
Lobby to building interior |  |  | A, B, C, D | 201 | New/Exist |  |  |  |  | F04 Entry
Mail room from Corridor |  |  | A, C | 203 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  | X | 18
Main Computer Room from Corridor |  |  | A, C | 217 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  | X | X | X |  | X | 18
Main Mechanical and Electrical Rooms from Corridor |  |  | A, C | 228 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 8, 18
Medical Media Equipment Storage from Corridor |  |  | A, C | 219 | New/Exist | X |  |  |  | F07 Store-room |  | X | X |  |  | X | X
Medical Supply Storage from Corridor |  |  | A, C | 214 | New/Exist | X | X | [8 empty] | X | X
Narcotics Vault from Pharmacy Cache |  |  | A | 212 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  | X | X |  |  | X | 18
Office of Information and Technology from Corridor |  |  | A, C | 216 | New/Exist | X | X |  |  | F07 Store-room |  | X | X |  | X | X | X
Pharmacy Cache from Corridor |  |  | A, C | 210 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  | X | X | X |  |  | 11, 18
Pharmacy Dispensing Area from Corridor |  |  | A | 211 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  |  | 18
Pharmacy Manufacturing Area from Corridor |  |  | A | 211 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  | X | X | X |  |  | 11, 18
Radioactive Materials Areas from Corridor |  |  | A, C | 223 | New/Exist | X |  | X |  | F07 Store-room |  | X |  |  | X | X | X |  |  | 8, 18
Security Control Center from Corridor |  |  | A | 204 | New/Exist | X |  | X |  | F07 Store-room |  | X |  |  |  | X |  |  |  | 9, 10, 18
Security Guard Station from Corridor |  |  | A | 206 | New/Exist | X |  |  |  | F07 Store-room |  | X |  |  |  | X
Telecommunications Main Distribution Frame Room |  |  | A, C | 218 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  | X | 18
Telecommunications Rooms and Electric Closets from Corridor |  |  | A, C | 218 | New/Exist |  |  |  | X | F07 Store-room | [5 empty] | X
Veterans' Records from Corridor |  |  | A, C | 213 | New/Exist | X |  | X | X | F07 Store-room |  | X |  |  |  | X | X |  | X | 12, 18
Weapon Storage/Armory from Security Control Center |  |  | A | 221 | New/Exist | X |  | X | X | F07 Store-room | X | X |  | X | X | X | X |  | X | 13, 18
Child Care/Child Development Center
Primary entrance and Exit |  |  | A, B, C, D | 112 | New | X | X |  |  |  | X | X |  | X |  | X |  |  |  | 1
Primary entrance and Exit |  |  | A, B, C, D | 112 | Exist | [10 empty] | X
Roof Access |  |  | A, C | 116 | New/Exist |  |  |  | X | F07 Store-room | [5 empty] | X
Roof Hatch |  |  | Not Applic. | 115 | New/Exist |  |  |  | X | [6 empty] | X |  |  |  | 17
Community Living Center/Nursing Home Care Unit
Egress |  |  | A, C | 104 | New/Exist |  |  |  |  | F01 Exit | [5 empty] | X | X |  |  | 2
Emergency Access |  |  | A | 110 | New/Exist |  |  |  | X | F07 Store-room
Guard House at Site Perimeter |  |  | A, B | 114 | New/Exist |  |  |  | X | F07 Store-room | [9 empty] | 9
Loading Dock (Overhead) |  |  | Overhead | 108 | New/Exist | X | [9 empty] | X
Loading Dock (Swinging) |  |  | A, C | 107 | New | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  | X | 18
Loading Dock (Swinging) |  |  | A, C | 107 | Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X
Public Entrances |  |  | A, B, C, D | 101 | New/Exist | X | X |  |  |  | X | X | X | X |  | X |  |  |  | 1, 4
Roof Access |  |  | A, C | 116 | New/Exist |  |  |  | X | F07 Store-room | [5 empty] | X
Roof Hatch |  |  | Not Applic. | 115 | New/Exist |  |  |  | X | [6 empty] | X |  |  |  | 17
Staff |  |  | A, B, C, D | 103 | New/Exist | X | X |  |  | F04 Entry | X | X | X | X |  | X |  |  |  | 2, 3, 4
Storage |  |  | A, C | 109 | New/Exist | X |  |  |  | F07 Store-room | [9 empty] | 7, 8
Tunnel |  |  | A | 111 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X |  |  | 8
Utility Connections (Commercial Power and Med Gas Stor) |  |  | A, C | 111 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X |  |  | 8
Utility Connections (Demarc Room) |  |  | A, C | 113 | New/Exist |  |  |  |  | F07 Store-room | [9 empty] | 8
Building Systems Room from Corridor |  |  | A, C | 228 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 8, 18
Canteen Retail Store from Corridor |  |  | A, B, C, D | 207 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X
Canteen Storage Room |  |  | A, C | 208 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X
Central Linen Storage and Distribution from Corridor |  |  | A, C | 215 | New/Exist | X | X | [8 empty] | X | X
Elevator Equipment Room from Corridor |  |  | A, C | 228 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 8, 18
Fire Control Center to Building Interior |  |  | A | 224 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X |  |  | 8
Lobby to building interior |  |  | A, B, C, D | 201 | New/Exist |  |  |  |  | F04 Entry
Mail room from Corridor |  |  | A, C | 203 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 18
Main Computer Room from Corridor |  |  | A, C | 217 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  | X | X | X |  |  | 18
Mechanical and Electrical Rooms from Corridor |  |  | A, C | 228 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 8, 18
Medical Media Equipment Storage from Corridor |  |  | A, C | 219 | New/Exist | X |  |  |  | F07 Store-room |  | X | X |  |  | X | X
Medical Supply Storage from Corridor |  |  | A, C | 214 | New/Exist | X |  | X | X | [6 empty] | X | X |  |  | 18
Office of Information and Technology from Corridor |  |  | A, C | 216 | New/Exist | X | X |  |  | F07 Store-room |  | X | X |  | X | X | X
Pharmacy Cache from Corridor |  |  | A, C | 210 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  | X | X | X |  |  | 11, 18
Psychiatric Unit Exit Only |  |  | A | 232 | New/Exist |  |  |  |  | F01 Pass-age | X |  | X |  |  | X | X |  |  | 16
Psychiatric Unit from Public Areas |  |  | A | 231 | New/Exist | X |  | X | X | F01 Pass-age | X |  | X |  |  | X |  |  |  | 16, 18
Radioactive Materials Areas from Corridor |  |  | A, C | 223 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  | X | X | X |  |  | 8, 18
Security Control Center from Corridor |  |  | A | 204 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 9, 10, 18
Security Guard Station from Corridor |  |  | A | 206 | New/Exist | X |  |  |  | F07 Store-room |  | X | X |  |  | X
Telecommunications Rooms and Electric Closets from Corridor |  |  | A, C | 218 | New/Exist |  |  |  |  | F07 Store-room
Veterans' Records from Corridor |  |  | A, C | 213 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  |  | 12, 18
Hospital
Egress |  |  | A, C | 104 | New/Exist |  |  |  |  | F01 Exit | [5 empty] | X | X |  |  | 2
Emergency Access |  |  | A | 110 | New/Exist |  |  |  | X | F07 Store-room
Emergency Department (Ambulance) |  |  | C | 105 | New/Exist | X | [13 empty] | 5
Emergency Department (Ambulatory) |  |  | A, C | 106 | New/Exist | X |  |  |  | F12 Exit Lock | [9 empty] | 6
Guard House at Site Perimeter |  |  | A, B | 114 | New/Exist |  |  |  | X | F07 Store-room | [9 empty] | 9
Loading Dock (Overhead) |  |  | Overhead | 108 | New/Exist | X | [9 empty] | X
Loading Dock (Swinging) |  |  | A, C | 107 | New | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  | X | 18
Loading Dock (Swinging) |  |  | A, C | 107 | Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X
Public Entrances |  |  | A, B, C, D | 101 | New/Exist | X | X |  |  |  | X | X | X |  |  | X |  |  |  | 1
Roof Access |  |  | A, C | 116 | New/Exist |  |  |  | X | F07 Store-room | [5 empty] | X
Roof Hatch |  |  | Not Applic. | 115 | New/Exist |  |  |  | X | [6 empty] | X |  |  |  | 17
Staff |  |  | A, B, C, D | 103 | New/Exist | X | X |  |  | F04 Entry | X | X | X |  |  | X |  |  |  | 2, 3, 6
Storage (non-pilferable items) |  |  | A,C | 109 | New/Exist |  |  |  | X | F07 Store-room | [9 empty] | 7, 8
Storage (pilferable items) |  |  | A, C | 109 | New/Exist | X |  |  | X | F07 Store-room |  | X | X |  |  | X |  |  | X | 7, 8
Tunnel |  |  | A | 111 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X |  |  | 8
Utility Connections (Commercial Power and Med Gas Stor) |  |  | A, C | 111 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X |  |  | 8
Utility Connections (Demarc Room) |  |  | A, C | 113 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X |  |  |  | 8
Agent Cashier from Corridor |  |  | A | 209 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  | X | 18
Animal Research Facility or Vivarium from Public Areas |  |  | A, C | 222 | New/Exist | X |  | X | X | F07 Store-room | X | X | X |  | X | X | X |  |  | 14,18
BSL-3 Laboratory Suites from Public Areas |  |  | A, C | 230 | New/Exist | X |  | X | X |  | X | X | X |  | X | X | X |  | X | 1, 18
Building Systems Room from Corridor |  |  | A, C | 228 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 8,18
Canteen Retail Store from Corridor |  |  | A, B, C, D | 207 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X
Canteen Storage Room |  |  | A, C | 208 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  |  | 18
Central Linen Storage and Distribution from Corridor |  |  | A, C | 215 | New/Exist | X | X | [8 empty] | X | X
Credit Union from Public Areas |  |  | A, C | 209 | New/Exist | X | X |  |  | F07 Store-room |  | X | X |  |  | X | X
Elevator Equipment Room from Corridor |  |  | A, C | 228 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 8,18
Evidence Storage from Corridor |  |  | A | 220 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  | X | 13,18
Fire Control Center to Building Interior |  |  | A | 224 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X |  |  | 8,18
Holding Area |  |  | A | 205 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  | X | 10,18
Interstitial Space from Stairs |  |  | A, C | 234 | New/Exist | X | X |  |  | F07 Store-room |  | X | X |  |  | X | X |  | X
Laboratories (Clinical and Research) from Public Areas |  |  | A, C | 222 | New/Exist | X |  | X | X | F07 Store-room | X | X | X | X | X | X | X |  |  | 14,18
Lobby to building interior |  |  | A, B, C, D | 201 | New/Exist |  |  |  |  | F04 Entry
Mail room from Corridor |  |  | A, C | 203 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 18
Main Computer Room from Corridor |  |  | A, C | 217 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  | X | X | X |  | X | 18
Mechanical and Electrical Rooms from Corridor |  |  | A, C | 228 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 8,18
Medical Media Equipment Storage from Corridor |  |  | A, C | 219 | New/Exist | X |  |  |  | F07 Store-room |  | X | X |  |  | X | X
Medical Supply Storage from Corridor |  |  | A, C | 214 | New/Exist | X |  | X | X | [6 empty] | X | X |  |  | 18
Narcotics Vault from Pharmacy Cache |  |  | A | 212 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  | X | X | X |  | X | 18
Office of Information and Technology from Corridor |  |  | A, C | 216 | New/Exist | X | X |  |  | F07 Store-room |  | X | X |  | X | X | X
Pharmacy Cache from Corridor |  |  | A, C | 210 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  | X | X | X |  |  | 11,18
Pharmacy Dispensing Area from Corridor |  |  | A | 211 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  |  | 18
Pharmacy Manufacturing Area from Corridor |  |  | A | 211 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  | X | X | X |  |  | 11,18
Psychiatric Unit Exit Only |  |  | A | 232 | New/Exist |  |  |  |  | F01 Pass-age | X |  |  | X |  | X |  |  |  | 16
Psychiatric Unit from Public Areas |  |  | A | 231 | New/Exist | X |  | X | X | F01 Pass-age | X |  |  | X |  | X |  |  |  | 16,18
Radioactive Materials Areas from Corridor |  |  | A, C | 223 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  | X | X | X |  |  | 8,18
Restricted or Controlled Access Area from Corridor |  |  | A, C | 227 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  |  | 8,18
Restricted or Controlled Access Floor from Elevator |  |  | Elevator Door | 225 | New/Exist | X |  | X | X | [6 empty] | X | X |  |  | 15,18
Restricted or Controlled Access Floor from Stair |  |  | A | 226 | New/Exist | X |  | X | X | Exit 13 |  | X |  |  | X | X | X |  |  | 8,18
Security Control Center from Corridor |  |  | A | 204 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  | X | 9, 10, 18
Security Guard Station from Corridor |  |  | A | 206 | New/Exist | X |  |  |  | F07 Store-room |  | X | X |  |  | X
Select Agent Rooms |  |  | A, C | 229 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  | X | 8,18
Telecommunications Main Distribution Frame (MDF) Room |  |  | AC | 218 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 18
Telecommunications Rooms/IDF Closets and Electric Closets from Corridor |  |  | A, C | 218 | New/Exist |  |  |  | X | F07 Store-room | [5 empty] | X
Veterans' Records from Corridor |  |  | A, C | 213 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  | X | 12,18
Weapon Storage/Armory from Security Control Center |  |  | A | 221 | New/Exist | X |  | X | X | F07 Store-room | X | X | X |  | X | X | X |  | X | 13,18
National Cemetery Administration
Administration Building - Public Entrance and Exit |  |  | A, B, C, D | 118 | New/Exist |  | X |  |  | F04 Entry | X |  |  | X | [5 empty] | 5
Maintenance/Storage Building Pedestrian Entrance |  |  | A | 114 | New/Exist | X |  |  |  | F04 Entry | X
Maintenance/Storage Building Vehicular Entrance |  |  | Overhead | 117 | New/Exist
Public Information Center - Public Entrance and Exit |  |  | A, B, C, D | 118 | New/Exist |  | X |  |  | F04 Entry | X |  |  | X | [5 empty] | 5
Administration Building - Telecom. Rms, Electric Clos & IT Server Clos. |  |  | A | 236 | New/Exist | X |  |  |  | F07 Store-room | [9 empty] | 8
Administration Building - Lobby to Building Interior |  |  | A, B, C, D | 235 | New/Exist | X |  |  |  | F04 Entry
Administration Building - Records Storage Closet, incl. FAX |  |  | A | 235 | New/Exist | X |  |  |  | F07 Store-room |  | X | [7 empty] | 8
Maintenance/Storage Building - Equipment and Supply Storage Rooms |  |  | A, C | 214 | New/Exist |  |  |  |  | F07 Store-room | [9 empty] | 8
Maintenance/Storage Building - Telecom. Rooms & Electric Clos. from Corridor |  |  | A, C | 218 | New/Exist |  |  |  |  | F07 Store-room | [9 empty] | 8
Public Information Center - Telecom. Rooms & Electric Clos. |  |  | A | 218 | New/Exist |  |  |  |  | F07 Store-room | [9 empty] | 8
A
Research Facilities and Vivaria
Egress |  |  | A, C | 104 | New/Exist |  |  |  |  | F01 Exit | [5 empty] | X | X |  |  | 2
Emergency Access |  |  | A | 110 | New/Exist |  |  |  | X | F07 Store-room
Guard House at Site Perimeter |  |  | A, B | 114 | New/Exist |  |  |  | X | F07 Store-room | [9 empty] | 9
Loading Dock (Overhead) |  |  | Overhead | 108 | New/Exist | X | [9 empty] | X
Loading Dock (Swinging) |  |  | A, C | 107 | New | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  | X | 18
Loading Dock (Swinging) |  |  | A, C | 107 | Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X
Public Entrances |  |  | A, C | 102 | New/Exist | X | X |  |  |  | X | X | X | [6 empty] | 1, 2, 4
Roof Access |  |  | A, C | 116 | New/Exist |  |  |  | X | F07 Store-room | [5 empty] | X
Roof Hatch |  |  | Not Applic. | 115 | New/Exist |  |  |  | X | [6 empty] | X |  |  |  | 17
Staff |  |  | A, C | 102 | New/Exist | X | X |  |  |  | X | X | X |  |  | X |  |  |  | 1, 2
Storage (non-pilferable items) |  |  | A,C | 109 | New/Exist |  |  |  | X | F07 Store-room | [5 empty] | X |  |  |  | 7,8
Storage (pilferable items) |  |  | A, C | 109 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  | X | 7, 8, 18
Tunnel |  |  | A | 111 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X |  |  | 8
Utility Connections (Commercial Power and Med Gas Stor) |  |  | A, C | 111 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X |  |  | 8
Utility Connections (Demarc Room) |  |  | A, C | 113 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X |  |  |  | 8
Animal Research Facility or Vivarium from Public Areas |  |  | A, C | 222 | New/Exist | X |  | X | X | F07 Store-room | X | X | X |  | X | X | X |  | X | 14,18
BSL-3 Laboratory Suites from Public Areas |  |  | A, C | 230 | New/Exist | X |  | X | X |  | X | X | X |  | X | X | X |  | X | 1,18
Building Systems Room from Corridor |  |  | A, C | 228 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 8,18
Elevator Equipment Room from Corridor |  |  | A, C | 228 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  | X | X |  |  |  | 8,18
Fire Control Center to Building Interior |  |  | A | 224 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X |  |  | 8
Interstitial Space from Stairs |  |  | A, C | 234 | New/Exist | X | X |  |  | F07 Store-room |  | X | X |  |  | X | X |  | X
Laboratories (Clinical and Research) from Public Areas |  |  | A, C | 222 | New/Exist | X | X |  |  | F07 Store-room | X | X | X |  | X | X | X |  |  | 14
Lobby to building interior |  |  | A, C | 202 | New/Exist | X | X |  |  |  | X | X | X |  |  | X |  |  |  | 1
Main Computer Room from Corridor |  |  | A, C | 217 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  | X | X | X |  | X | 18
Mechanical and Electrical Rooms from Corridor |  |  | A, C | 228 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 8,18
Medical Media Equipment Storage from Corridor |  |  | A, C | 219 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  |  | 18
Office of Information and Technology from Corridor |  |  | A, C | 216 | New/Exist | X | X |  |  | F07 Store-room |  | X | X |  | X | X | X
Radioactive Materials Areas from Corridor |  |  | A, C | 223 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  | X | X | X |  | X | 8,18
Restricted or Controlled Access Area from Corridor |  |  | A, C | 227 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  |  | 8,18
Restricted or Controlled Access Floor from Elevator |  |  | Elevator Door | 225 | New/Exist | X |  | X | X | [6 empty] | X | X |  |  | 15,18
Restricted or Controlled Access Floor from Stair |  |  | A | 226 | New/Exist | X |  | X | X | Exit 13 |  | X | X |  |  | X | X |  |  | 8,18
Security Guard Station from Corridor |  |  | A | 206 | New/Exist | X |  |  |  | F07 Store-room |  | X | X |  |  | X
Select Agent Rooms |  |  | A, C | 229 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  |  | 8,18
Telecommunications Main Distribution Frame (MDF) Room |  |  | A, C | 218 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  | X | 18
Telecommunications Rooms/Closets (IDFs) and Electric Closets from Corridor |  |  | A, C | 218 | New/Exist |  |  |  | X | F07 Store-room | [5 empty] | X
Vivarium |  |  | A, C | 222 | New/Exist | X |  | X | X | Exit 01 |  | X | X |  |  | X | X |  |  | 18
Vivarium Exit |  |  | A, C | 222 | New/Exist | [10 empty] | X | X
Veterans Benefits Administration
Egress |  |  | A, C | 104 | New/Exist |  |  |  |  | F01 Exit | [5 empty] | X | X |  |  | 2
Emergency Access |  |  | A | 110 | New/Exist |  |  |  | X | F07 Store-room
Guard House at Site Perimeter |  |  | A, B | 114 | New/Exist |  |  |  | X | F07 Store-room | [9 empty] | 9
Loading Dock (Overhead) |  |  | Overhead | 108 | New/Exist | X | [9 empty] | X
Loading Dock (Swinging) |  |  | A, C | 107 | New | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  | X | 18
Loading Dock (Swinging) |  |  | A, C | 107 | Exist |  |  |  |  | F07 Store-room | [5 empty] | X
Public Entrances |  |  | A, B, C, D | 101 | New/Exist | X | X |  |  |  | X | X | X |  |  | X |  |  |  | 1, 2, 4
Roof Access |  |  | A, C | 116 | New/Exist |  |  |  | X | F07 Store-room | [5 empty] | X
Roof Hatch |  |  | Not Applic. | 115 | New/Exist |  |  |  | X | [6 empty] | X |  |  |  | 17
Staff |  |  | A, B, C, D | 103 | New/Exist | X | X |  |  | F04 Entry | X | X | X | X |  | X |  |  |  | 1, 2
Storage (non-pilferable items) |  |  | A, C | 109 | New/Exist |  |  |  | X | F07 Store-room | [5 empty] | X |  |  |  | 7, 8
Storage (pilferable items) |  |  | A, C | 109 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  | X | 7, 8, 18
Tunnel |  |  | A | 111 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X |  |  | 8
Utility Connections (Commercial Power) |  |  | A, C | 111 | MC New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X |  |  | 8
Utility Connections (Demarc Room) |  |  | A, C | 113 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X |  |  |  | 8
Building Systems Room from Corridor |  |  | A, C | 228 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 8,18
Elevator Equipment Room from Corridor |  |  | A, C | 228 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 8,18
Fire Control Center to Building Interior |  |  | A | 224 | New/Exist |  |  |  |  | F07 Store-room | [5 empty] | X | X |  |  | 8
Mail room from Corridor |  |  | A, C | 203 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 18
Main Computer Room from Corridor |  |  | A, C | 217 | New/Exist | X | X |  |  | F07 Store-room |  | X | X |  | X | X | X
Mechanical and Electrical Rooms from Corridor |  |  | A, C | 228 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 8,18
Office of Information and Technology from Corridor |  |  | A, C | 216 | New/Exist | X | X |  |  | F07 Store-room |  | X | X |  | X | X | X
Security Control Center from Corridor |  |  | A | 204 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X |  |  |  | 9, 10, 18
Security Guard Station from Corridor |  |  | A | 206 | New/Exist | X |  |  |  | F07 Store-room |  | X | X |  |  | X
Telecommunications Rooms and Electric Closets from Corridor |  |  | A, C | 218 | New/Exist |  |  |  |  | F07 Store-room
Veterans' Records from Corridor |  |  | A, C | 213 | New/Exist | X |  | X | X | F07 Store-room |  | X | X |  |  | X | X |  |  | 12,18
Veterans Benefits Administration (where VBA is only tenant)
Public Entrances |  |  | A, B, C, D | 101 | New/Exist | X | X |  |  |  | X | X | X |  |  | X |  |  |  | 1, 2, 4
Roof Access |  |  | A, C | 116 | New/Exist |  |  |  | X | F07 Store-room | [5 empty] | X
Roof Hatch |  |  | Not Applic. | 115 | New/Exist |  |  |  | X | [6 empty] | X |  |  |  | 17
Staff |  |  | A, B, C, D | 103 | New/Exist | X | X |  |  | F04 Entry | X | X | X |  |  | X |  |  |  | 1, 2
Lobby to building interior |  |  | A, B, C, D | 201 | New/Exist |  |  |  |  | F04 Entry
Notes
1. | Magnetic lock or electric strike |  | 9. | FEBR (30 minutes with Tools/UL 752, Level 3) | [6 empty] | 18. | All locks shall be field selectable Fail Safe/Fail Secure. The term Fail Secure indicates the lock will remain secure when in fail mode. Fail Secure shall always permit emergency egress functions of the lock. In these circumstances an bypass feature; such as, conventional key and lock, shall be provided to allow access from the unsecure side. Magnetic locks shall not fail secure.
2. | Alarmed exit |  | 10. | One-way glass
3. | Magnetic lock, electric strike or ANSI F04 Entrance lock |  | 11. | 30 minute forced entry
4. | Intercom to reception, information or guard desk |  | 12. | 15 minute forced entry
5. | Manual operation during power outage |  | 13. | FEBR (15 minutes/Level III)
6. | Intercom to guard station |  | 14. | ANSI F07 Storeroom lock and magnetic lock or electric strike
7. | Card reader or ANSI F07 Storeroom lock |  | 15. | Elevator door control
8. | No glazing |  | 16. | Glazed door, monitor door at Nurses' Station
|  |  | 17. | Padlock from the inside