## DESIGNER'S SCHEDULE USE
DESIGNER'S SCHEDULE USE INSTRUCTIONS
1. MAKE ALL SCHEDULES PROJECT SPECIFIC.
2. COORDINATE ALL VA PLUMBING STANDARD SCHEDULES WITH VA MASTER SPECIFICATIONS.
3. COORDINATE ALL VA PLUMBING STANDARD SCHEDULES WITH VA STANDARD DETAILS.
4. SI UNITS ARE IN FORMULA FORMAT. COPY AND PASTE IN CELL BELOW FOR EACH USE.

## SS220511-01
VIBRATION ISOLATION SCHEDULE | [7 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | EQUIPMENT AND/OR SERVICE | TYPE BASE | TYPE ISOLATOR | MIN STATIC DEFLECTION |  | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | IN | [mm]
5-VI1 | B1100 | 5-SF1 | B | S | 1.1 | 28 | ---
DESIGNER NOTE
REFER TO SELECTION GUIDE IN HVAC CRITERIA AND TO MANUFACTURER'S DATA FOR TYPE OF ISOLATOR AND MINIMUM STATIC DEFLECTION. LIST EQUIPMENT NOT REQUIRING ISOLATORS (PUMPS IN SEPARATE CHILLER BUILDING, ETC.). INDICATE THAT ISOLATORS WILL NOT BE REQUIRED TO VERIFY THAT EQUIPMENT WAS NOT OVERLOOKED.

## SS220511-02
EQUIPMENT CONNECTION SCHEDULE | [16 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | EQUIPMENT DESCRIPTION | WASTE PIPE |  | VENT PIPE |  | COLD WATER |  | HOT WATER |  | COMPRESSED AIR |  | VACUUM |  | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  |  | IN | [mm] | IN | [mm] | IN | [mm] | IN | [mm] | IN | [mm] | IN | [mm]
HD-102 | C105 | BIO-MEDICAL | EXHAUST HOOD | 2 | 50 | 1.5 | 38 | .75 | 19 | .75 | 19 | .5 | 13 | .5 | 13 | INDIRECT WASTE
DESIGNER NOTE:
◊ SHOW ALL EQUIPMENT FOR KITCHEN, DIAGNOSTICS AND TREATMENT. BIOMEDICAL ETC. COORDINATE PIPE SIZE WITH CUT SHEETS.

## SS221123-01
PLUMBING PUMP SCHEDULE
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | CIRCULATING FLUID | [10 empty] | ELECTRICAL MOTOR | [6 empty] | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | FLUID | FLOW |  | HEAD |  | NPSH AVAILABLE |  | TEMPERATURE |  | SP. GR. | MIN. % EFF | NOMINAL POWER |  | PHASE | VOLT | MAX RPM | SPEED CONTROL | REMARKS
[6 empty] | GPM | [L/s] | FT | [kPa] | FT | [kPa] | °F | [°C] |  |  | HP | [kW]
1-PP1 | 1220 MER | MAIN HOSPITAL | HOT WATER RECIR | CENT | DOMESTIC WATER | 80 | 5 | 60 | 960 | NA | NA | 140 | 60 | 1 | 70 | 2 | 1.5 | 3 | 460 | 1750 | CONSTANT | ----
DESIGNER NOTE
◊ ANTIFREEZE FLUID IS USUALLY PROPYLENE GLYCOL WATER (PGW). ADJUST FLOW, HEAD, AND POWER FOR FLUID PUMPED.

## SS221123-02
PACKAGE BOOSTER PUMP SCHEDULE | [26 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | CIRCULATING FLUID | [10 empty] | PRESSURE TRANSMITTER SETPOINT |  | OULET BUFFER TANK ACCEPTANCE VOLUME |  | ELECTRICAL MOTOR | [6 empty] | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | FLUID | NO PUMPS | FLOW EA. PUMP |  | HEAD EA. PUMP |  | MIN NPSH AVAIL | TEMPERATURE |  | SP GR | % EFF |  |  |  |  | NOMINAL POWER, EA. |  | PHASE | VOLT | MAX RPM | SPEED CONTROL | REMARKS
[7 empty] | GPM | [L/s] | FT | [M] |  | °F | [°C] |  |  | PSIG | [kPa] | GAL | [L] | HP | [kW]
1-BP1 | MECH ROOM | HOSPITAL PRESSURE ZONE #2 | DOMESTIC BOOSTER PUMP | END SUCTION | DOMESTIC COLD WATER | 3 | 380 | 24 | 80 | 24 | N/A | 50 | 10 | 1 | 68 | 92 | 630 | 54 | 200 | 7.5 | 5.6 | 3 | 460 | 1750 | VARIABLE | -----
DESIGNER NOTE:
INSURE BOOSTER PUMP IS ON EMERGENCY POWER.

## SS221216-01
STORAGE TANK SCHEDULE | [17 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | TYPE | SYSTEM TEMPERATURE RANGE |  |  |  | MAX OPERATING PRESSURE |  | RELIEF VALVE |  | MIN VOLUME |  | INLET PIPE SIZES |  | OUTLET PIPE SIZES |  | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  | MIN |  | MAX
|  |  | °F | [°C] | °F | [°C] | PSIG | [kPa] | PSIG | [kPa] | GAL | [L] | IN | [mm] | IN | [mm]
7-ST5 | B1100 | GLASS LINED POTABLE WATER | 60 | 16 | 140 | 60 | 80 | 550 | 100 | 690 | 2000 | 7600 | 3 | 75 | 3 | 75 | -----
DESIGNER NOTE
◊ COORDINATE WITH STRUCTURAL DRAWING TO SHOW SADDLE SUPPORTS.

## SS221500-01
AIR COMPRESSOR SCHEDULE | [20 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | INLET AIRFLOW |  | DISCHARGE PRESSURE |  | RECEIVER SIZE |  | RECEIVER DIMENSIONS, DIA X LENGTH |  | ELECTRIC POWER [60 Hz] | [5 empty] | OPER WEIGHT | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[13 empty] | NO. MOTORS | POWER EA. |  | PHASE | VOLT | RPM
[5 empty] | CFM | [L/s] | PSIG | [kPa] | GAL | [L] | IN | [mm] |  | HP | [kW]
1-AC5 | B1100 | PATIENT CARE | MEDICAL AIR | DUPLEX OILLESS SCROLL | 64 | 24 | 120 | 830 | 200 | 760 | 36X84 | [900X2100] | 2 | 10 | 7.5 | 3 | 460 | 1750 | 3550 | -----
DESIGNER NOTE:
◊ PROVIDE SEPARATE/INDEPENDENT AIR COMPRESSOR SYSTEMS FOR :
1. MEDICAL AIR COMPRESSOR
2. LABORATORY AIR COMPRESSOR
3. GENERAL/PLANT AIR COMPRESSOR
4. DENTAL AIR COMPRESSOR

## SS223111-01
WATER SOFTENER SCHEDULE | [24 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | INCOMING WATER HARDNESS | CONTINUOUS FLOW RATE |  | PEAK FLOW RATE |  | INLET PRESSURE |  | BACK WASH FLOW RATE |  | CAPACITY/ SALT DOSAGE |  |  | TANK SIZE (DIAM) |  | SALT CAPACITY OF BRINE TANK |  | POWER REQUIRED |  |  | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[14 empty] | SALT DOSAGE | MIN. BED (SUBFILL OF SAND) | MAX. BED
[5 empty] | PPM | GPM | [L/s] | GPM | [L/s] | PSIG | KPA | GPM | [L/s] | LBS/ CUFT | [KGr]/[LB] | [KGr]/[LB] | IN | [mm] | LB | [KG] | AMP | PHASE | VOLT
1-WS1 | A123 | HOSPITAL | HEATING WATER | ION EXCHANGE | 200 | 150 | 9.5 | 250 | 16 | 110 | 760 | 75 | 4.7 | 15 | 750 / 375 | 1350 / 675 | 72 | 1800 | 3500 | 1600 | 10 | 1 | 120 | ---

## SS223111-02
WATER FILTER SCHEDULE | [8 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | TYPE | CAPACITY |  | AUTOMATIC VALVE PRESSURE RANGE |  | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  |  | GPM | [L/s] | PSIG | [kPa]
1-WF1 | B109 | DOMESTIC WATER | CHARCOAL | 230 | 15 | 60 | 410 | -----
DESIGNER NOTE:
◊ SEE 2.3 ACTIVATED CARBON FILTER UNDER PLUMBING SPECIFICATION 22 67 19.16 REVERSE OSMOSIS WATER EQUIPMENT

## SS223300-01
ELECTRIC WATER HEATER SCHEDULE | [17 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | STORAGE CAPACITY |  | RECOVERY @ 70 °F [21°C] RISE |  | TIME TO RECOVER CONTENTS, MINUTES | RELIEF VALVE SETTING |  | NO OF ELEMENTS | ELECTIRCAL INPUT |  |  |  | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | GAL | [L] | GAL/HR | [L/HR] |  | PSIG | [kPa] |  | TOTAL kW | kW PER ELEMENT | PHASE | VOLT
24-WH2 | A132 | NURSING HOME | DOMESTIC HOT WATER | LARGE VOLUME ELECTRIC | 500 | 1900 | 650 | 2500 | 40 | 100 | 690 | 8 | 130 | 18 | 3 | 480 | -----
1-WH-10 | D1106 | SHOP | DOMESTIC HOT WATER | SMALL UNDER COUNTER | 5 | 19 | 8.5 | 32 | 45 | 70 | 480 | 1 | 1.5 | 1.5 | 1 | 120

## SS223400-01
GAS FIRED WATER HEATER SCHEDULE | [21 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | STORAGE CAPACITY |  | RECOVERY @ 70 °F [21°C] RISE |  | TIME TO RECOVER CONTENTS, MINUTES |  |  | FUEL |  |  |  |  | ELECTRICAL MOTOR |  |  |  | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[10 empty] | RELIEF VALVE SETTING |  | TYPE | INLET PRESSURE |  | FLOW |  | NOMINAL POWER, EA. |  | PHASE | VOLT
[5 empty] | GAL | [L] | GAL/HR | [L/HR] |  | PSIG | [kPa] |  | IN WG | [Pa] | CFH | [L/H] | HP | [kW]
7-WH2 | C105 | NURSING HOME | DOMESTIC HOT WATER | SEMI INSTANTANEOUS | 750 | 2800 | 340 | 1300 | 70 | 100 | 690 | NATURAL GAS | 18 | 4500 | 200 | 5700 | .25 | 190 | 1 | 120 | ---

## SS223400-02
DOMESTIC WATER THERMAL EXPANSION TANK SCHEDULE | [19 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | TYPE | SYSTEM TEMPERATURE RANGE |  |  |  | INITIAL PRESSURE IN TANK |  | MAX OPERATING PRESSURE |  | RELIEF VALVE PSIG [kPA] |  | MIN TANK VOLUME |  | MIN ACCEPT VOLUME |  | PIPE SIZE TO TANK |  | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  | MIN |  | MAX
|  |  | °F | [°C] | °F | [°C] | PSIG | [kPa] | PSIG | [kPa] | PSIG | [kPa] | GAL | [L] | GAL | [L] | IN | [mm]
1-ET27 | B1100 | POTABLE THERMAL EXPANSION TANK | 60 | 16 | 140 | 60 | 50 | 350 | 80 | 550 | 100 | 690 | 15 | 57 | 10.5 | 40 | .75 | 19 | -----

## SS223500-01
STEAM TO WATER HEAT EXCHANGER SCHEDULE | [22 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | WATER CONDITIONS | [7 empty] | STEAM PRESSURE |  |  |  | CONTROL VALVE |  | TRAP |  |  | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | FLOW |  | EWT |  | LWT |  | WPD |  | ENT CONTROL VALVE |  | ENT HEAT EXCHANGER |  |  |  | TRAP NO | CAPACITY
[5 empty] | GPM | [L/s] | °F | [°C] | °F | [°C] | FT | [kPa] | PSIG | [kPa] | PSIG | [kPa] | LB/HR | [KG/HR] |  | LB/HR | [KG/HR]
1-HEX1 | 0190 MER | PATIENT CARE | DOMESTIC HOT WATER | DOUBLE WALL, SEMI INSTANTANEOUS, SHELL & TUBE | 170 | 11 | 60 | 16 | 140 | 60 | 16 | 48 | 15 | 100 | 7 | 48 | 7000 | 3200 | 1-TP2 | 11000 | 5000 | ----
Note on F4: Wenda McMahan : what is quantity? Should it be "FLUID," is that column out of place?

## SS223500-02
LIQUID TO LIQUID HEAT EXCHANGER SCHEDULE | [21 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | HOT SIDE | [7 empty] | COLD SIDE | [7 empty] | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | FLOW |  | EWT |  | LWT |  | WPD |  | FLOW |  | EWT |  | LWT |  | WPD
[5 empty] | GPM | [L/s] | °F | [°C] | °F | [°C] | FT | [M] | GPM | [L/s] | °F | [°C] | °F | [°C] | FT | [M]
1-HEX2 | 0190 MER | DIETECTICS | KITCHEN BOOSTER | PLATE & FRAME | 200 | 13 | 200 | 93 | 180 | 82 | 14 | 42 | 50 | 3.2 | 50 | 10 | 180 | 82 | 16 | 48 | -----

## SS223500-03
STORAGE TANK WITH HEAT EXCHANGER SCHEDULE | [24 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | TYPE | SYSTEM TEMPERATURE RANGE |  |  |  | FLOW RATE |  | MAX OPERATING PRESSURE |  | RELIEF VALVE |  | MIN TANK VOLUME |  | STEAM PRESSURE |  |  |  | CONTROL VALVE |  | TRAP |  |  | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  | MIN |  | MAX | [9 empty] | ENT CONTROL VALVE |  | ENT HEAT EXCHANGER |  |  |  | TRAP NO | CAPACITY
|  |  | °F | [°C] | °F | [°C] | GPM | [L/S] | PSIG | [kPa] | PSIG | [kPa] | GAL | [L] | PSIG | [kPa] | PSIG | [kPa] | LB/HR | [KG/HR] |  | LB/HR | [KG/HR]
7-ST1 | B1100 | GLASS LINED, TANK & TUBE | 60 | 16 | 140 | 60 | 150 | 9.5 | 80 | 550 | 100 | 690 | 2000 | 7600 | 15 | 100 | 7 | 48 | 7000 | 3200 | 1-TP4 | 11000 | 5000 | -----

## SS223500-04
STEAM BOOSTER WATER HEATER SCHEDULE | [18 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | TYPE | FLOW |  | EWT |  | LWT |  | STEAM PIPE SIZE |  | CONDENSATE PIPE SIZE |  | STEAM DEMAND |  | STEAM PRESSURE |  | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  |  | GPM | [L/s] | °F | [°C] | °F | [°C] | IN | [mm] | IN | [mm] | LB/HR | [KG/HR] | PSIG | [kPa]
10-HX5 | C105 | KITCHEN BOOSTER HEATER | SHELL & TUBE | 40 | 2.5 | 130 | 54 | 180 | 82 | 1 | 25 | .75 | 19 | 1000 | 450 | 30 | 210 | -----

## SS224000-01
PLUMBING FIXTURE SCHEDULE | [14 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | DESCRIPTION | WASTE PIPE |  | VENT PIPE |  | COLD WATER |  | HOT WATER |  | WASTE FIXTURE UNITS | WATER FIXTURE UNITS | WRIST BLADE HANDLES | ELECTRIC SENSOR | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  | IN | [mm] | IN | [mm] | IN | [mm] | IN | [mm]
PP-1 | WATER CLOSET, WALL HUNG, ELONGATED BOWL, 1.6 GPF | 4 | 100 | 2 | 50 | 1.25 | 31 | .5 | 13 | 4 | 4 | N/A | YES | ---
PP-101 | WATER CLOSET FLOOR MTD | 3 | 75 | 2 | 50 | 1.25 | 31 |  |  | 6 | 10 | N/A | NO | BED PAN WASHER
PP-102 | WATER CLOSET FLOOR MTD | 3 | 75 | 2 | 50 | 1.25 | 31 |  |  | 6 | 10 | N/A | YES
PP-103 | WATER CLOSET, WALL HUNG | 3 | 75 | 2 | 50 | 1.25 | 31 |  |  | 6 | 10 | N/A | YES
PP-201 | URINAL WALL HUNG | 2 | 50 | 1.5 | 38 | .75 | 19 |  |  | 2 | 5 | N/A | YES | WHEELCHAIR
PP-202 | URINAL WALL HUNG | 2 | 50 | 1.5 | 38 | .75 | 19 |  |  | 2 | 5 | N/A | NO
PP-302 | BATH TUB WITH SHOWER | 2 | 50 | 1.5 | 38 | .5 | 13 | .5 | 13 | 2 | 2 | N/A | NO
PP-401 | LAVATORY | 2 | 50 | 1.5 | 38 | .5 | 13 | .5 | 13 | 2 | 2 | N/A | NO
PP-402 | LAVATORY ELBOW CONTROL | 2 | 50 | 1.5 | 38 | .5 | 13 | .5 | 13 | 2 | 2 | N/A | NO
PP-403 | LAVATORY FOOT PEDAL CONTROL | 2 | 50 | 1.5 | 38 | .5 | 13 | .5 | 13 | 2 | 2 | N/A | NO
PP-414 | LAVATORY | 2 | 50 | 1.5 | 38 | .5 | 13 | .5 | 13 | 2 | 2 | N/A | NO
PP-501 | SINK SERVICE | 3 | 75 | 2 | 50 | .75 | 19 | .75 | 19 | 3 | 4 | N/A | NO
PP-502 | SINK SERVICE FLOOR MOUNTED | 3 | 75 | 2 | 50 | .75 | 19 | .75 | 19 | 3 | 4 | N/A | NO
PP-505 | SINKSERVICE CLINIC | 3 | 75 | 2 | 50 | 1 | 25 | .75 | 19 | 3 | 4 | N/A | NO | RIM FLUSHING
PP-604 | ELECTRIC WATER COOLER | 2 | 50 | 1.5 | 38 | .5 | 13 |  |  | 1 | 1 | N/A | NO
PP-701 | SHOWER | 2 | 50 | 1.5 | 38 | .5 | 13 | .5 | 13 | 2 | 2 | N/A | NO
PP-706 | EMERGENCY SHOWER |  |  |  |  | 1.25 | 31 |  |  |  | 10 | N/A | NO
PP-801 | WALL HYDRANT |  |  |  |  | .75 | 19 |  |  |  | 5 | N/A | NO
PP-902 | WALL HYDRANT |  |  |  |  | 0.75 | 19 | 0.75 | 19 |  | 5 | N/A | NO

## SS226200-01
VACUUM PUMP SCHEDULE | [17 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE UNIT | RECEIVER SIZE |  | VACUUM PRESSURE |  | CFM DELIVERY @ VACUUM PRESSURE (SI) |  | ELECTRIC POWER | [5 empty] | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[11 empty] | NO. PUMPS | POWER EACH |  | PHASE | VOLT | RPM
[5 empty] | GAL | [L] | in Hg | [kPa] | SCFM | STANDARD [L/s] |  | HP | [Kw]
1-VP1 | ROOM 6 | CAMPUS | MEDICAL VACUUM | DRY TRIPLEX | 200 | 760 | 19 | 64 | 138 | 65 | 3 | 7.5 | 5.6 | 3 | 460 | 1750
DESIGNER NOTE:
◊ PROVIDE SEPARATE/INDEPENDENT VACUUM SYSTEMS FOR:
1. MEDICAL VACUUM
2. LABORATORY VACUUM

## SS226300-01
GAS PRESSURE REGULATOR | [15 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | CAPACITY |  | INLET PRESSURE |  | INLET SIZE |  | OUTLET PRESSURE |  | OUTLET SIZE |  | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | CU FT/HR | [L/HR] | PSIG | [kPa] | IN | [mm] | PSIG | [kPa] | IN | [mm]
5-GPR2 | SITE | NHCU | NATURAL GAS | PILOT | 12000 | 340000 | 30 | 210 | 2 | 50 | 5 | 35 | 4 | 100 | -----
Note on F5: Wenda: need conversion

## SS226300-02
FOOD SERVICE STEAM OR GAS DEMAND SCHEDULE | [16 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | DESCRIPTION | STEAM PIPE SIZE |  | CONDENSATE PIPE SIZE |  | STEAM DEMAND |  | STEAM PRESSURE |  | NAT GAS PIPE SIZE |  | NAT GAS DEMAND |  | GAS PRESSURE |  | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  | IN | [mm] | IN | [mm] | LB/HR | [KG/HR] | PSIG | [kPa] | IN | [mm] | BTUH | [W] | PSIG | [kPa]
13702 | DIETECTICS DISHWASHER | 1 | 25 | .75 | 19 | 3000 | 1400 | 15 | 100 | NA | NA | NA | NA | NA | NA | ----

## SS226719_16-01
PACKAGED REVERSE OSMOSIS SCHEDULE | [21 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | INCOMING WATER PPM DISOLVED SOLIDS | PRODUCT CAPACITY |  | FEED FLOW |  | REJECT FLOW |  | CLEANING FLOW |  | NO. VESSELS | MEMBRANES PER VESSEL | VESSEL ARRAY | PUMP ELECTRICAL |  |  |  | REMARKS | SUBMITTAL TRACKING NOS | MANUFACTURER | MODEL NO | SERIAL NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[17 empty] | POWER |  | PHASE | VOLT
[6 empty] | GPM | [LPM] | GPM | [LPM] | GPM | [LPM] | GPM | [LPM] |  |  |  | HP | [kW]
1-RO5 | C105 | RESEARCH WING | LABORATORY COLD WATER | MULTISTAGE, SINGLE PASS | 300 | 10.5 | 40 | 16.2 | 62 | 5.7 | 22 | 10 | 38 | 3 | 3 | 1:1:1 | 10 | 7.5 | 3 | 480 | ---

## METRIC CONVERSIONS
METRIC SOFT CONVERSION RULES
ENGLISH UNIT QUANTITY | ENGLISH UNITS | METRIC UNIT QUANTITY | METRIC UNITS
0 | F | -17.7778 | C
1 | FT | 300 | mm
1 | INCH | 25 | mm
0.25 | INCH | 6.4 | mm
0.5 | INCH | 15 | mm
0.75 | INCH | 19 | mm
1 | CFM | 0.472 | L/s
1 | GPM | 3.8 | LPM
1 | GPM | 0.06309 | LPS
1 | PSI | 6.9 | kPa
1 | FT H20 | 15.94 | kPa
1 | IN W.G. | 250 | Pa
1 | BTUH | 0.293 | WATTS
1 | TON | 0.2844 | KILOWATTS
3.41 | BTUH | 1 | WATTS
1 | HP | 746 | WATTS
1 | LB | 0.454 | KG
1 | LB/HR | 0.454 | KG/HR
NOTES
1. ROUND TO 2 SIGNIFICANT FIGURES FOR ALL CONVERSIONS
FOR INFORMATION PURPOSES ONLY
ENGLISH | METRIC | CONVERSION | EQUATION
-16 | -27 | TEMPERATURE,[⁰F TO ⁰C] | IF(A25>32,ROUND(((A25-32)/1.8),2-LEN(INT(((A25-32)/1.8)))),ROUND(((A25-32)/1.8),3-LEN(INT(((A25-32)/1.8)))))ROUND(((A25-32)/1.8),2-LEN(INT(((A25-32)/1.8))))
100 | 30000 | DISTANCE, [FT TO mm] | ROUND(A26*300,2-LEN(INT(A26*300)))
100 | 2500 | DISTANCE, [INCH TO mm] | ROUND(A27*25,2-LEN(INT(A27*25)))
100 | 47 | AIRFLOW, [CFM TO L/s] | ROUND(A28*.472,2-LEN(INT(A28*.472)))
100 | 380 | FLOW, [GPM TO LPM] | ROUND(A29*3.8,2-LEN(INT(A29*3.8)))
100 | 6.3 | FLOW, [GPM TO L/s] | ROUND(A30*.06309,2-LEN(INT(A30*0.06309)))
100 | 690 | PRESSURE, [PSIG TO kPa] | ROUND(A31*6.9,2-LEN(INT(A31*6.9)))
0.75 | 190 | PRESSURE, [IN W.G. TO Pa] | ROUND(A32*250,2-LEN(INT(A32*250)))
40000 | 12000 | POWER, [BTUH TO WATTS] | ROUND(A33*.293,2-LEN(INT(A33*.293)))
1 | 750 | POWER, [HP TO WATTS] | ROUND(A34*746,2-LEN(INT(A34*746)))
100 | 75 | POWER, [HP TO KILOWATTS] | ROUND(A35*.746,2-LEN(INT(A35*.746)))
100 | 45 | WEIGHT [LB TO KG] | ROUND(A36*.454,2-LEN(INT(A36*.454)))
100 | 45 | STEAM FLOW, [LB/HR TO KG/HR] | ROUND(A37*.454,2-LEN(INT(A37*.454)))
100 | 28 | CLG EFFECT [TONS TO KW] | ROUND(A38*.2844,2-LEN(INT(A38*.2844)))
40 | 640 | PRESS, [FT H20 TO kPa] | ROUND(A39*15.94,2-LEN(INT(A39*15.94)))
100 | 30 | DISTANCE, [FT TO M] | ROUND(A40*.3,2-LEN(INT(A40*.3)))
1 | 3.8 | VOLUME, [Gal TO L] | ROUND(A41*3.785,2-LEN(INT(A41*3.785)))