## UPDATES
Listing of Revisions to Specific HVAC Schedules Included
Schedule | Date Updated | Schedule Group
Boiler Plant · Natural Gas Flowmeter Schedule 23 09 11-01 | 2017-12-01 | 23 09 11
Boiler Plant · Oil Flowmeter Schedule 23 09 11-02 | 2017-12-01
Boiler Plant · Water Flowmeter Schedule 23 09 11-03 | 2017-12-01
Boiler Plant · Water Flow Control Valve Schedule 23 21 11-01 | 2017-12-01 | 23 21 11
Boiler Plant · Blowoff Tank Water Outlet Temperature Control Valve Schedule 23 21 11-02 | 2017-12-01
Boiler Plant · Steam Pressure Reducing Valve Schedule 23 21 11-03 | 2017-12-01
Boiler Plant · Steam Trap Schedule 23 21 11-04 | 2017-12-01
Steam to Water Heat Exchanger Schedule 23 21 13-01 | 2017-12-01 | 23 21 13
Liquid to Liquid Heat Exchanger Schedule 23 21 13-02 | 2017-12-01
Expansion Tank Schedule 23 21 13-03 | 2017-12-01
Air Separator Schedule 23 21 13-04 | 2017-12-01
Steam Humidifier Schedule 23 22 13-01 | 2017-12-01 | 23 22 13
Steam Pressure Relief Valve Schedule 23 22 13-02 | 2017-12-01
Building · Steam Pressure Reducing Valve Schedule 23 22 13-03 | 2017-12-01
Building · Steam Trap Schedule 23 22 13-04 | 2017-12-01
Clean Steam Generator Schedule 23 22 13-05 | 2017-12-01
Steam Condensate Pump Schedule 23 22 23-01 Steam Condensate Pumps | 2017-12-01 | 23 22 23
Pressure Powered Condensate Pump Schedule 23 22 23-01 | 2017-12-01
Boiler Plant · Pump Schedule 23 50 11-01 | 2017-12-01 | 23 50 11
Boiler Plant · Fuel Oil Pump Schedule 23 50 11-02 | 2017-12-01
Boiler Plant · Fuel Oil Heater Schedule 23 50 11-03 | 2017-12-01
Boiler Plant · Fuel Oil Tanks (Burner Fuel) Schedule 23 50 11-04 | 2017-12-01
Boiler Plant · Condensate Storage Tank Schedule 23 50 11-05 | 2017-12-01
Boiler Plant · Blowoff Tank Schedule 23 50 11-06 | 2017-12-01
Boiler Plant · Economizer Schedule, Flue Gas/Feedwater Heat Exchangers 23 50 11-07 | 2017-12-01
Boiler Plant · Air Compressor Schedule 23 50 11-08 | 2017-12-01
Boiler Plant · Refrigerated Air Dryer Schedule 23 50 11-09 | 2017-12-01
Boiler Plant · Steam Vent Silencer Schedule 23 50 11-10 | 2017-12-01
Boiler Plant · Continuous Blowdown Heat Exchanger Schedule 23 50 11-11 | 2017-12-01
Boiler Plant · Chemical Feed Systems, Pump Type Schedule 23 50 11-12 | 2017-12-01
Boiler Plant · Emergency Gas Shut-off Valves Schedule 23 50 11-13 | 2017-12-01
Boiler Plant · Low Pressure Hot Water Boiler, Packaged Type, Factory Assembled 23 52 25-01 NEW SCHEDULE | 2017-12-01 | 23 52 25
Boiler Plant · Water Tube Steam Boiler Schedule, Packaged Type, Shop Assembled 23 52 33-01 Water Tube Boilers | 2017-12-01 | 23 52 33
Boiler Plant · Fire Tube Steam Boiler Schedule, Packaged Type, Shop Assembled 23 52 39-01 | 2017-12-01 | 23 52 39
Hot Water Heating Boiler Schedule 23 52 39-02 | 2017-12-01
Steam Unit Heater Schedule 23 82 00-05 | 2017-12-01 | 23 82 00
Steam Heating Coil Schedule 23 82 16-03 | 2017-12-01 | 23 82 16

## TABLE OF CONTENTS
SCHEDULE |  | CADD FILE NAME | SPECIFICATION SECTION NAME
DIVISION 23
1 | Unit Cooler Schedule (Refrigeration Service) | 11 41 21-01 | Walk-in Coolers and Freezers
2 | Air Cooled Condensing Unit Schedule (Refrigeration Service) | 11 41 21-02
3 | Water Cooled Condensing Unit Schedule (Refrigeration Service) | 11 41 21-03
4 | Fume Hood Exhaust Schedule | 11 53 13-01 | Lab Hoods
5 | Biological Safety Cabinet Exhaust Schedule | 11 53 53-01 | Biological Safety Cabinets
6 | HVAC Design Data | 23 05 11-01 | Common Work HVAC
7 | Vibration Isolation Schedule | 23 05 41-01 | Noise and Vibration Control
8 | Boiler Plant · Natural Gas Flowmeter Schedule | 23 09 11-01 | Instrumentation and Control System for Boiler Plant
9 | Boiler Plant · Oil Flowmeter Schedule | 23 09 11-02
10 | Boiler Plant · Water Flowmeter Schedule | 23 09 11-03
11 | Air Flow Measuring Device Schedule | 23 09 23-01 | Direct Digital Control
12 | Smoke and Combination Fire/Smoke Damper Schedule | 23 09 23-02
13 | Hoistway Vent Damper Schedule | 23 09 23-03
14 | Boiler Plant · Water Flow Control Valve Schedule | 23 21 11-01 | Boiler Plant Piping Systems
15 | Boiler Plant · Blowoff Tank Water Outlet Temperature Control Valve Schedule | 23 21 11-02
16 | Boiler Plant · Steam Pressure Reducing Valve Schedule | 23 21 11-03
17 | Boiler Plant · Steam Trap Schedule | 23 21 11-04
18 | Steam to Water Heat Exchanger Schedule | 23 21 13-01 | Hydronic Piping
19 | Liquid to Liquid Heat Exchanger Schedule | 23 21 13-02
20 | Expansion Tank Schedule | 23 21 13-03
21 | Air Separator Schedule | 23 21 13-04
22 | Pump Schedule | 23 21 23-01 | Hydronic Pumps
23 | Steam Humidifier Schedule | 23 22 13-01 | Steam and Condensate Piping
24 | Steam Pressure Relief Valve Schedule | 23 22 13-02
25 | Building · Steam Pressure Reducing Valve Schedule | 23 22 13-03
26 | Building · Steam Trap Schedule | 23 22 13-04
27 | Clean Steam Generator Schedule | 23 22 13-05
28 | Steam Condensate Pump Schedule | 23 22 23-01 | Steam Condensate Pumps
29 | Water Filter Schedule (Side Stream) | 23 25 00-01 | HVAC Water Treatment
30 | Solid Separator Schedule (Side Stream) | 23 25 00-02
31 | Intake/Exhaust Hood Schedule | 23 31 00-01 | HVAC Ducts and casings
32 | Sound Attenuating Device Schedule | 23 31 00-02
33 | Canopy Hood Schedule | 23 31 00-03
34 | Fan Schedule | 23 34 00-01 | HVAC Fans
35 | Air Terminal Unit Sizing Schedule | 23 36 00-01 | Air Terminal Units
36 | Single Duct Air Terminal Unit Schedule | 23 36 00-02
37 | Air Flow Control Valve Schedule | 23 36 00-03
38 | Air Device Schedule (Supply) | 23 37 00-01 | Air Outlets and Inlets
39 | Air Device Schedule (Linear) | 23 37 00-02
40 | Air Device Schedule (Return) | 23 37 00-03
41 | Room Air Balance Schedule | 23 37 00-04
42 | Air Filter Schedule | 23 40 00-01 | HVAC Air Cleaning Devices
43 | Boiler Plant · Pump Schedule | 23 50 11-01 | Boiler Plant Mechanical Equipment
44 | Boiler Plant · Fuel Oil Pump Schedule | 23 50 11-02
45 | Boiler Plant · Fuel Oil Heater Schedule | 23 50 11-03
46 | Boiler Plant · Fuel Oil Tanks (Burner Fuel) Schedule | 23 50 11-04
47 | Boiler Plant · Condensate Storage Tank Schedule | 23 50 11-05
48 | Boiler Plant · Blowoff Tank Schedule | 23 50 11-06
49 | Boiler Plant · Economizer Schedule, Flue Gas/Feedwater Heat Exchangers | 23 50 11-07
50 | Boiler Plant · Air Compressor Schedule | 23 50 11-08
51 | Boiler Plant · Refrigerated Air Dryer Schedule | 23 50 11-09
52 | Boiler Plant · Steam Vent Silencer Schedule | 23 50 11-10
53 | Boiler Plant · Continuous Blowdown Heat Exchanger Schedule | 23 50 11-11
54 | Boiler Plant · Chemical Feed Systems, Pump Type Schedule | 23 50 11-12
55 | Boiler Plant · Emergency Gas Shut-off Valves Schedule | 23 50 11-13
56 | Boiler Plant · Water Tube Steam Boiler Schedule, Packaged Type, Shop Assembled | 23 52 33-01 | Water Tube Boilers
57 | Boiler Plant · Fire Tube Steam Boiler Schedule, Packaged Type, Shop Assembled | 23 52 39-01 | Fire Tube Boilers
58 | Hot Water Heating Boiler Schedule | 23 52 39-02
59 | Water Cooled Chiller Schedule | 23 64 00-01 | Packaged Water Chillers
60 | Air Cooled Chiller Schedule | 23 64 00-02
61 | Remote Condenser Chiller Schedule | 23 64 00-03
62 | Air Cooled Condensing Unit Schedule (Air Conditioning Service) | 23 64 00-04
63 | Cooling Tower Schedule | 23 65 00-01 | Cooling Towers
64 | Heat Pipe Air to Air Exchanger Schedule | 23 72 00-01 | Air to Air Energy Recovery Equipment
65 | Rotary Air to Air Heat Recovery Wheel Schedule | 23 72 00-02
66 | Make-Up Air Heating and Ventilating Unit Schedule | 23 73 00-01 | Indoor Central Station Air Handling Units
67 | Air Handling Unit Schedule | 23 73 00-02
68 | Packaged Evaporative Cooler Schedule | 23 73 00-03
69 | Air Washer Schedule | 23 73 00-04
70 | Room Heating and Cooling Unit Schedule (Thru-Wall, Electrical Heating Coil, Self Contained Refrigeration) | 23 81 00-01 | Decentralized Unitary HVAC Equipment
71 | Water Cooled Packaged Air Conditioner Schedule | 23 81 00-02
72 | Single Packaged Air Conditioner Gas/Electric Schedule (Rooftop) | 23 81 00-03
73 | Single Packaged Air Conditioner Heat Pump Schedule (Rooftop) | 23 81 00-04
74 | Split System Air Conditioner Gas/Electric Schedule | 23 81 00-05
75 | Split System Air Conditioner Heat Pump Schedule | 23 81 00-06
76 | Water Source Heat Pump Schedule | 23 81 46-01 | Water Source Unitary Heat Pumps
77 | Hot Water Unit Heater Schedule | 23 82 00-01 | Convection Heating and Cooling Units
78 | Hot Water Finned Tube Radiation Schedule | 23 82 00-02
79 | Radiant Ceiling Panel Schedule (Electric) | 23 82 00-03
80 | Radiant Ceiling Panel Schedule (Hydronic) | 23 82 00-04
81 | Steam Unit Heater Schedule | 23 82 00-05
82 | Cooling Only Two Pipe Fan Coil Unit Schedule | 23 82 00-06
83 | Heating Only Two Pipe Fan Coil Unit Schedule | 23 82 00-07
84 | Four Pipe Fan Coil Unit Schedule | 23 82 00-08
85 | Electric Duct Mounted Heating Coil Schedule | 23 82 00-09
86 | Electric Unit Heater Schedule | 23 82 00-10
87 | Chilled Water Cooling Coil Schedule | 23 82 16-01 | Air Coils
88 | Hot Water Heating Coil Schedule | 23 82 16-02
89 | Steam Heating Coil Schedule | 23 82 16-03
90 | Direct Expansion Cooling Coil Schedule | 23 82 16-04
91 | Heat Recovery System Run Around Water Coil Schedule | 23 82 16-05

## EQUIPMENT SCHEDULE INSTRUCTIONS
INSTRUCTIONS FOR USE
VA HVAC Design Manual for Hospitals, Clinical Additions, and Psychiatric Care
Equipment Schedules
Introduction: These equipment schedules are used throughout the entire life of the building.
Phase I - Design Phase, Architect/Engineer (A/E) Submission to the VA (Peer Reviewer)
Step 1: | Download the Excel VA HVAC Design Manual Equipment Schedules workbook from the VA TIL: http://www.va.gov/facmgt/standard/details.asp.
NOTE: It is a project requirement to use only these Equipment Schedules, and to use them as is.
Step 2: | Open the Equipment Schedules workbook, review the index, and delete any schedules you don't need. (To delete a schedule from the Excel workbook, right-click its tab at the bottom and select delete.)
Step 3: | Refer to Appendix 1-B.1 of the HVAC DM in the VA TIL (http://www,va.gov/facmgt/standard/dmnual/ dmmehosp_01.pdf) for an overview of the relationship between the HVAC DM, the Equipment Schedules and the CAFM process.
Refer to Appendix 1-C.1.5 of the HVAC DM in the VA TIL (http://www.va.gov/facmgt/standard/dmnual/dmmehosp_01.pdf) for the order of presentation for the schedules.
Refer to the A/E Checklists in the VA TIL (http://www.va.gov/facmgt/standard/ae_checklist.asp) for a listing of the applicable sections of the TIL for additional information on the data to be entered in the schedules.
A/E Submission Requirements (http://www.va.gov/facmgt/ae/des_sub.asp) require full calculation sets for all equipment selections. When approved, the calculations will ultimately appear in pop-up data boxes in the Excel spreadsheet files in the CAFM system. The design engineer shall indicate the basis for design (manufacturer and equipment model number) for each piece of equipment.
Step 4: | The examples included in the schedules are intended only to illustrate their use. Remove all examples from the schedules before submission.
Step 5: | Complete all schedules that pertain to the specific project. If additional schedules are needed, the A/E shall prepare them using formats similar to those used for these schedules.
The SI units are autocalculated when the IP units are entered. If you require additional rows on a schedule, copy the formulae for the SI calculations from the existing rows.
(See the Column Guide for more information on the elements of the schedules.)
Printing the Workbook: To print the entire workbook, select "All" for the print range and choose a printer that has both Tabloid (11" x 17") and Letter (8.5" x 11") paper. The schedules will print on the paper size designated for each them.
Step 6: | Insert the completed schedules into the CAD drawings as follows. If you paste the cells from each schedule as a "Microsoft Excel Worksheet" and save the Excel schedule spreadsheet and AutoCAD drawing to your local drive, any time the Excel spreadsheet is updated, the AutoCAD drawing will be updated automatically.
Step 7: | The schedules contain both Notes and Designer Notes. Before submission, erase the Designer Notes (highlighted in yellow) from the sheets which are only intended to guide the A/E. Hide the yellow columns for later use by contractor/vendor, and finally, the VA Medical Center.
At DD2, the A/E shall show the manufacturer and model number used as the basis of design (show in "Remarks" and include with submission). Update data as required at CD1 and CD2.
Prior to issuing for bid, erase any Manufacturer data in the Remarks columns.
Step 8: | Upon award of the construction contract, the contractor will unhide the hidden columns in the schedules and complete them with the final Manufacturer submittal data and bills of material.
IMPORTANT: Do not include specific manufacturer or model data on any of the schedules submitted to the contractor.
Phase II - Architect/Engineer (A/E) forwards Excel schedules to the contractor
Step 1: | Once contract awarded, unhide the yellow columns.
Step 2: | Send the schedules, both the Excel spreadsheets and as drawings, to the contractor to enter the manufacturer, model, and other equipment-specific data. If the database supports it, the contractor will include the commissioning report and test and balance data as well.
Phase III - Construction Phase
Step 1: | Upon award of the construction contract, the contractor will complete the hidden columns in the schedules with the final submittal data and bills of material.
Step 2: | Insert the completed schedules into the final as-built CAD drawings. The contractor will send the Excel workbook to VA and A/E.
Step 3: | Throughout the course of construction, the Equipimeent Schedules shall be maintained by the contractor.
Phase IV - Closeout and Turnover to VA Medical Center
During the preparation of the final as-built drawings, the A/E shall verify the accuracy of all data on the equipment schedules. In addition to the drawings, the A/E shall turn over to the medical center a complete set of final Excel spreadsheets with all columns displayed.

## ABBREVIATIONS
Abbreviations
EQUIPMENT
Abbreviation | Description | Abbreviation | Description
AAHX | Air to Air Heat Exchanger | FD | Fire Damper
ACCH | Air-Cooled Chiller | FF | Final Filter
ACCU | Air-Cooled Condensing Unit | FHX | Flue Gas/Feedwater Heat Exchanger
ACU | Air-Conditioning Unit | FM | Flowmeter
AF | After-Filters | FOP | Fuel Oil Pump
AFCV | Air Flow Control Valve | FOT | Fuel Oil Tank
AFMD | Air Flow Measuring Device | FOHX | Fuel Oil Heat Exchanger
AHU | Air-Handling Unit | FTR | Fin Tube Radiation
AS | Air Separator
AW | Air Washer | H | Humidifier
|  | HC | Heating Coil
B | Boiler | HD | Hood
BFT | Boiler Plant Fire Tube | HP | Heat Pump
BHW | Hot Water Heating Boiler | HRP | Hydronic Radiant (Ceiling) Panel
BHX | Boiler Blowdown Heat Exchanger | HTM | Humidifier Terminal
BSC | Biological Safety Cabinets | HUM | Humidifier Unit Mounted
BT | Boiler Tank | HW | Hot Water
BTCU | Blow Off Tank Control Valve | HWHC | Hot Water Heating Coil
BWT | Boiler Plant Water Tube | HWC | Hot Water Coil
|  | HWP | Heating Hot Water Pump
CC | Cooling Coil | HWUH | Hot Water Unit Heater
CFP | Chemical Feed Pump | HVD | Hoistway Vent Damper
CHP | Chilled Water Pump | HX | Heat Exchanger
CHW | Chilled Water
COMP | Compressor Unit | LLHX | Liquid to Liquid Heat Exchanger
CP | Condensate Pump
CS | Condensate Storage Tank | MAU | Make-up Air Unit
CT | Cooling Tower
CU | Condensing Unit | NGFM | Natural Gas Flow Meter
CUH | Cabinet Unit Heater | NPSH | Net Positive Suction Head
CV | Constant Volume
CWCC | Chilled Water Cooling Coil | OAI | Outside Air Intake
CWP | Condenser Water Pump | OFM | Oil Flowmeter
DDC | Direct Digital Controls | P | Pump
DPA | Differential Pressure Assembly | PF | Pre-Filter
DPS | Differential Pressure Switch/Sensor | PHC | Preheat Coil
DX | Direct-Expansion | PTAC | Packaged Terminal Air Conditioner
DXCC | Direct-Expansion Cooling Coil
|  | RAD | Refrigerant Air Dryer
EC | Evaporative Cooler | RAHX | Rotary Air Heat Exchanger
ECC | Engineering Control Center | RCCH | Remote Condenser Chiller
ECU | Evaporative Condenser Unit | RF | Return Fan
EDH | Electric Duct Heater | RG | Return Grille
EF | Exhaust Fan | RR | Return Register
EGS | Emergency Gas Shutoff | RTU | Roof Top Unit
EH | Exhaust Hood
ERC | Electric Reheat Coil | SAD | Sound Attenuating Device
ERP | Electric Radiant Panel | SD | Smoke Detector
ET | Expansion Tank | SD | Supply Air Diffuser
EUH | Electric Unit Heater | SDPR | Smoke Damper
EWC | Evaporative Water Cooler | SF | Supply Fan
|  | SH | Steam Humidifier
F/SDPR | Combination Fire Smoke Damper | SHC | Steam Heating Coil
FCU | Fan Coil Unit (4 Pipe) | SP | Static Pressure
FCUC | Fan Coil Unit Cooling Only | SP GR | Specific Gravity
FCUH | Fan Coil Unit Heating Only | SPD | Supply Process and Distribution
Abbreviations
EQUIPMENT
Abbreviation | Description | Abbreviation | Description
SPRV | Steam Pressure Reducing Valve
SR | Supply Air Register
SSHX | Steam to Steam Heat Exchanger
SSR | Solid Separator
ST | Steam Trap
SUH | Steam Unit Heater
SV | Steam Pressure Reducing Valve
SVS | Steam Vent Silencer
SWHX | Steam to Water Heat Exchanger
TP | Trap
TU | Terminal Unit
UC | Unit Cooler
UH | Unit Heater
V | Valve
VAV | Variable Air Volume
VFD | Variable Frequency Drive
VI | Vibration Isolator
VPS | Variable Primary System
VSD | Variable Speed Drive
WC | Water Cooled
WCCH | Water Cooled Chiller
WCCU | Water Cooled Condensing Unit
WCHP | Water Cooled Heat Pump
WCPU | Water Cooled Packaged Unit
WCUH | Water Cooled Unit Heater
WF | Water Filter
WFCV | Water Flow Control Valve
WFM | Water Flowmeter
Abbreviations
UNITS OF MEASURE
Abbreviation | Description | Abbreviation | Description
APD | Air Side Pressure Drop | L/m | Liters Per Minute
|  | L/s | Liters Per Second
BHP | Brake Horse Power | LAT | Leaving Air Temperature
BTU | British Thermal Unit | LBS/HR | Pounds Per Hour
BTUH | British Thermal Unit per Hour | LF | Linear Foot (Feet)
|  | LGT | Leaving Glycol Temperature
C | Centigrade (Celsius) | LH | Latent Heat
CFM | Cubic Feet Per Minute | LVG | Leaving
CFH | Cubic Feet Per Hour | LWT | Leaving Water Temperature
CFT | Cubic Feet
CM | Cubic Meter | M | Meter
CM/s | Centimeter Per Second | MAX | Maximum
COP | Coefficient of Performance | MBH | 1000 BTUH
|  | MCA | Maximum Current Ampacity
Db | Dry-Bulb Temperature | MCA | Multichannel Analyzer
DB | Decibels | MERV | Minimum Efficiency Reporting Value
DEG | Degree | MHP | Motor Horsepower
DIA | Diameter | MIN | Minimum
DP | Dewpoint | MM | Millimeter
|  | M/s | Meters Per Second
EAT | Entering Air Temperature | MTD | Mean Temperature Difference
EER | Energy Efficiency Ratio
EGT | Entering Glycol Temperature | NA | Not Applicable (also N/A)
ENT | Entering | NC | Noise Criteria
ESP | External Static Pressure | NOM | Nominal
EWT | Entering Water Temperature | NPLV | Non-standard Part Load Value
F | Fahrenheit | PA | Pascal
FPM | Feet Per Minute | PSI | Pounds Per Square Inch
FPS | Feet Per Second | PSIG | Pounds Per Square Inch-Gage
FT | Feet
FT-LB | Foot-Pound | RAF | Radio-Frequency
|  | RAT | Return Air Temperature
GA | Gauge | RLA | Run Load Ampere
GAL | Gallons | RPM | Revolutions Per Minute
GPD | Gallons Per Day
GPH | Gallons Per Hour | SAT | Supply Air Temperature
GPM | Gallons Per Minute | SCFM | Standard Cubic Feet Per Minute
|  | SQ FT | Square Foot (Feet)
HP | Horsepower | SQ M | Square Meter
HZ | Hertz
|  | TD | Temperature Difference
IN | Inches | TSP | Total Static Pressure
IN HG | Inches of Mercury
IN WG | Inch Water Gauge | W | Watts
IN-LB | Inch-Pound | Wb | Wet-Bulb (Temperature)
IPLV | Integrated Part Load Value | WG | Water Gage
|  | WPD | Water Side Pressure Drop
kg | Kilogram
kg/HR | Kilogram Per Hour | YR | Year
kPa | Kilo Pascal
kW | Kilowatt
kWh | Kilowatt Hour
L | Liter
L/h | Liters Per Hour
Abbreviations
GENERAL
Abbreviation | Description | Abbreviation | Description
A/E | Architects and Engineers | VHA | Veterans Health Administration
ARI | Air Conditioning and Refrigeration Institute
ASME | American Society Of Mechanical Engineers
BMT | Bone Marrow Transplant
CD-1 | Construction Design (Submission1)
CD-2 | Construction Design (Submission2)
CENT | Centrifugal
CO2 | Carbon Dioxide
CW | Cold Water (Potable)
DD-1 | Design Development (Submission1)
DD-2 | Design Development (Submission2)
EA | Exhaust Air
ETO | Ethylene Oxide
HAC | Housekeeping Aide’s Closet
I/O | Input/Output
ICU | Intensive Care Unit
LPG | Liquid Propane Gas
MER | Mechanical Equipment Room
MRI | Magnetic Resonance Imaging
NG | Natural Gas
NOAA | National Oceanic & Atmospheric Administration
OA | Outside Air
OR | Operating Room
PGW | Propylene Glycol-Water Solution
PSS | Primary Secondary System
R/E | Return or Exhaust
RA | Return Air
RDS | Room Data Sheets
RO | Reverse Osmosis
SA | Supply Air
SCI | Spinal Code Injury
SD-1 | Schematic Design 1
SD-2 | Schematic Design 2
SEN | Sensible Heat
UL | Underwriter's Laboratory

## COLUMN GUIDE
Guide to Columns in the Equipment Schedules
Note: Refer to Equipment Schedule SS233400-01 as an example of the use of these columns.
Column | Description
Mark | This is a unique equipment number. The first digit of the identifier is the building number where the equipment is located (on the Medical Center campus). The rest of the alpha characters (2-4) comprise the abbreviation for this piece of equipment (see the Abbreviations tab). The last digit is the number of the occurrence of that particular equipment number -- first, second, third, and so on -- within the building.
In the Computer Aided Facility Management (CAFM) database, each Mark number is proceeded by the Project Number (including the Medical Center Identifier). This should ensure a totally unique number within the VA system.
Location | This is the identifier for the room in which the equipment is located.
Area Served | This is the identifier for the area, set of rooms, or building served by this piece of equipment.
System/Service | This is the system of which the equipment is a part or that it serves.
Technical Data | The remaining columns contain technical equipment attributes and are self-explanatory.
Yellow Columns
Submittal Track | The number assigned to each equipment submittal.
Manufacturer | During construction, the contractor will complete these columns with the actual installed manufactured equipment.
Model | The equipment model number assigned by the manufacturer.
Serial Number | To be completed during construction once the equipment has been shipped/installed.
Commissioning Report No | The number assigned to the commissioning report that describes the specific equipment.
Test and Balance | The number assigned to the T&B report describing the specific equipment.
O&M Tab No | The tab in the O&M Manual which covers maintenance for the specific equipment.
General Data | The remaining yellow columns are self-explanatory.

## METRIC
METRIC SOFT CONVERSION RULES
English Unit Quantity | English Units | Metric Unit Quantity | Metric Units
0 | F | -17.7778 | C
1 | FT | 300 | mm
1 | INCH | 25 | mm
0.25 | INCH | 6.4 | mm
0.5 | INCH | 15 | mm
0.75 | INCH | 19 | mm
1 | GAL. | 3.8 | Liters
1 | CFM | 0.472 | L/s
1 | GPM | 3.8 | L/m
1 | GPM | 0.06309 | LPS
1 | CFH | 0.472 | L/m
1 | PSI | 6.9 | kPa
1 | FT H20 | 15.94 | kPa
1 | IN W.G. | 250 | Pa
1 | BTUH | 0.293 | WATTS
1 | TON | 0.2844 | KILOWATTS
1 | MBH | 0.293 | KILOWATTS
3.41 | BTUH | 1 | WATTS
1 | HP | 746 | WATTS
1 | LB | 0.454 | kg
1 | LBS/HR | 0.454 | kg/HR
NOTES
1. FOR ALL CONVERSIONS, ROUND TO 2 SIGNIFICANT FIGURES.
2. THESE FORMULAS PROVIDED FOR INFORMATION PURPOSES ONLY.
ENGLISH | METRIC | CONVERSION | EQUATION
-16 | -27 | TEMPERATURE,[⁰F TO ⁰C]
100 | 30000 | DISTANCE, [FT TO mm] | IF(ISNUMBER(A27)=TRUE,ROUND(A27*300,2-LEN(INT(A27*300)))
100 | 2500 | DISTANCE, [INCH TO mm] | ROUND(A28*25,2-LEN(INT(A28*25)))
100 | 47 | AIR FLOW, [CFM TO L/s] | ROUND(A29*.472,2-LEN(INT(A29*.472)))
100 | 47 | AIR FLOW, [CFH to L/m] | ROUND(A29*.472,2-LEN(INT(A29*.472)))
100 | 380 | FLOW, [GPM TO L/m] | ROUND(A30*3.8,2-LEN(INT(A30*3.8)))
100 | 6.3 | FLOW, [GPM TO L/s] | ROUND(A31*.06309,2-LEN(INT(A31*0.06309)))
100 | 690 | PRESSURE, [PSIG TO kPa] | ROUND(A32*6.9,2-LEN(INT(A32*6.9)))
0.75 | 190 | PRESSURE, [IN W.G. TO Pa] | ROUND(A33*250,2-LEN(INT(A33*250)))
40000 | 12000 | POWER, [BTUH TO WATTS] | ROUND(A34*.293,2-LEN(INT(A34*.293)))
1 | 750 | POWER, [HP TO WATTS] | ROUND(A35*746,2-LEN(INT(A35*746)))
100 | 75 | POWER, [HP TO KILOWATTS] | ROUND(A36*.746,2-LEN(INT(A36*.746)))
1 | 0.3 | POWER, [MBH TO kW] | ROUND(A29*.293,2-LEN(INT(A29*.293)))
100 | 45 | WEIGHT [LB TO kg] | ROUND(A37*.454,2-LEN(INT(A373*.454)))
100 | 45 | STEAM FLOW, [LBS/HR TO kg/HR] | ROUND(A38*.454,2-LEN(INT(A38*.454)))
100 | 28 | CLG EFFECT [TONS TO kW] | ROUND(A39*.2844,2-LEN(INT(A39*.2844)))
40 | 120 | PRESS, [FT H20 TO kPa] | ROUND(A40*2.989,2-LEN(INT(A40*2.989)))
100 | 30 | DISTANCE, [FT TO M] | ROUND(A41*.3,2-LEN(INT(A41*.3)))
1 | 3.8 | VOLUME, [Gal TO L] | ROUND(A42*3.785,2-LEN(INT(A42*3.785)))
450 | 2.3 | VELOCITY, FPM to M/s | ROUND(A43*.00508,2-LEN(INT(A43*.00508)))

## SS114121-01
UNIT COOLER SCHEDULE (REFRIGERATION SERVICE) | [16 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | EVAPORATOR SECTION TEMP |  | CAPACITY |  | ROOM DESIGN TEMP |  | AIR FLOW |  | MOTOR |  |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[11 empty] | # | POWER EACH |  | PHASE | VOLT
|  |  | °F | [°C] | BTUH | [W] | °F | [°C] | CFM | [L/s] |  | HP | [W]
1-UC1 | B001 | CANTEEN FREEZER | -16 | -26.7 | 11200 | 3300 | -12 | -24.4 | 2800 | 1300 | 3 | 0.25 | 190 | 1 | 115 | 1 kW, 3ф/208V ELEC DEFROST
[6 empty] | 0 |  |  |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 |  |  | 0
NOTE
UNIT COOLER CAPACITY SHALL BE BASED ON A EVAPORATION TEMPERATURE 2°F [1.1 °C] HIGHER THAN SUCTION TEMPERATURE OF COMPRESSOR.
DESIGNER NOTES
1. THIS SCHEDULE SHALL BE USED ONLY FOR FREEZERS AND/OR REFRIGERATORS. INDICATE ELECTRIC-TYPE DEFROST WHEN REQUIRED.
2. FINAL DRAWING SIZE = 12 IN. WIDE

## SS114121-02
AIR COOLED CONDENSING UNIT SCHEDULE (REFRIGERATION SERVICE) | [21 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | CAPACITY |  | SUCTION TEMP |  | AMBIENT AIR |  | MAX COND TEMP |  | COMPRESSOR MOTOR |  |  |  |  | CONDENSER FAN MOTOR |  |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[11 empty] | # COMP | POWER |  | PHASE | VOLT | # COND. FAN | POWER |  | PHASE | VOLT
|  |  | BTUH | [W] | °F | [°C] | °F | [°C] | °F | [°C] |  | HP | [kW] |  |  |  | HP | [W]
1-ACCU1 | OUTSIDE YARD D2 | 1-UC1 | 11200 | 3300 | -18 | -27.8 | 95 | 35 | 110 | 43.3 |  | 3 | 2.2 | 3 | 460 |  | 0.33 | 250 | 1 | 277 | ----
|  |  |  | 0 | [8 empty] | 0 |  |  |  |  | 0
|  |  |  | 0 | [8 empty] | 0 |  |  |  |  | 0
|  |  |  | 0 | [8 empty] | 0 |  |  |  |  | 0
|  |  |  | 0 | [8 empty] | 0 |  |  |  |  | 0
|  |  |  | 0 | [8 empty] | 0 |  |  |  |  | 0
DESIGNER NOTES
1. PROVIDE COORDINATED SELECTION OF UNIT COOLER AND CONDENSING UNIT.
2. FINAL DRAWING SIZE = 16 IN. WIDE

## SS114121-03
WATER COOLED CONDENSING UNIT SCHEDULE (REFRIGERATION SERVICE) | [19 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | CAPACITY |  | SUCTION TEMP |  | WATER COOLED CONDENSER | [6 empty] | COMPRESSOR MOTOR |  |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[7 empty] | FLOW |  | EWT |  | LWT |  | COOLING SOURCE | # COMP | POWER |  | PHASE | VOLT
|  |  | BTUH | [W] | °F | [°C] | GPM | [L/m] | °F | [°C] | °F | [°C] |  |  | HP | [W]
1-WCCU1 | 0100 | 1-UC1 | 11200 | 3300 | -18 | -27.8 | 1.3 | 4.9 | 45 | 7.2 | 65 | 18.3 | CHW |  | 2 | 1500 | 3 | 460 | ----
|  |  |  | 0 |  |  |  | 0 | [7 empty] | 0
|  |  |  | 0 |  |  |  | 0 | [7 empty] | 0
|  |  |  | 0 |  |  |  | 0 | [7 empty] | 0
|  |  |  | 0 |  |  |  | 0 | [7 empty] | 0
|  |  |  | 0 |  |  |  | 0 | [7 empty] | 0
|  |  |  | 0 |  |  |  | 0 | [7 empty] | 0
|  |  |  | 0 |  |  |  | 0 | [7 empty] | 0
|  |  |  | 0 |  |  |  | 0 | [7 empty] | 0
NOTE
WHEN USING CHILLED WATER AS CONDENSER SOURCE, SIZE FOR A MINIMUM OF 20˚ F [11˚ C] TEMPERATURE RISE FOR CHILLED WATER.
DESIGNER NOTES
1. PROVIDE UNIT-MOUNTED MODULATING THREE-WAY CONTROL VALVE AND PUMP TO ENSURE MINIMUM CHILLED WATER FLOW/TEMPERATURE AS REQUIRED BY CONDENSING UNIT MANUFACTURER.
2. WATER-COOLED UNIT CANNOT USE POTABLE WATER TO WASTE.
3. COORDINATE WITH UNIT COOLER SELECTION.
4. FINAL DRAWING SIZE = 14 IN. WIDE

## SS115313-01
FUME HOOD EXHAUST SCHEDULE | [10 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | HOOD TYPE | HOOD SIZE (WIDTH) |  | EXHAUST |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | BELT ID | SHEAVE ID | PM NO
[6 empty] | AIR FLOW |  | APD HOOD ONLY
|  |  |  | IN | [mm] | CFM | [L/s] | IN WG | [Pa]
1-HD10 | ROOM 219 | EXHAUST SYSTEM 1-EF2 | H3 | 60 | 1500 | 1125 | 530 | 0.4 | 100 | SEE DETAIL FOR HEPA FILTER
1-HD11 | ROOM 221 | EXHAUST SYSTEM 1-EF11 | H7 | 48 | 1200 | 875 | 410 | 0.37 | 93 | -----
1-HD12 | ROOM 229 | EXHAUST SYSTEM 1-EF12 | H14 | 48 | 1200 | 875 | 410 | 0.37 | 93 | SEE DETAIL FOR WASH DOWN
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
NOTE
THE HOOD DATA (EXHAUST AIR VOLUME AND PRESSURE DROP) IS BASED ON A REPRESENTATIVE MAKE AND MODEL NUMBER. IN THE EVENT THE HOOD SELECTED AND FURNISHED BY THE CONTRACTOR HAS DIFFERENT HOOD DATA, THE CONTRACTOR SHALL BE RESPONSIBLE FOR MAKING NECESSARY MODIFICATIONS TO THE DESIGN AND CONSTRUCTION WITHOUT ANY ADDITIONAL COST TO THE GOVERNMENT.
DESIGNER NOTES
1. FUME HOODS PROVIDED UNDER ARCHITECTURAL EQUIPMENT.
2. RADIOISOTOPE HOODS ARE DESIGNATED AS VA TYPE H3; GENERAL PURPOSE CHEMICAL FUME HOODS ARE DESIGNATED AS VA TYPE H7. PERCHLORIC ACID HOODS ARE DESIGNATED AS VA TYPE H14.
3. FINAL DRAWING SIZE = 12 IN. WIDE

## SS115353-01
BIOLOGICAL SAFETY CABINET EXHAUST SCHEDULE | [10 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | HOOD TYPE | HOOD SIZE (WIDTH) |  | EXHAUST |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[6 empty] | AIR FLOW |  | APD HOOD ONLY
|  |  |  | IN | [mm] | CFM | [L/s] | IN WG | [Pa]
1-HD4 | ROOM 114 | EXHAUST SYSTEM 1-EF2 | CLASS II TYPE B1 | 48 | 1200 | 270 | 130 | 1 | 250 | -----
1-HD10 | ROOM 110 | EXHAUST SYSTEM 1-EF10 | CLASS II TYPE B2 | 72 | 1800 | 1150 | 540 | 1 | 250 | -----
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
NOTE
THE HOOD DATA (EXHAUST AIR VOLUME AND PRESSURE DROP) IS BASED ON A REPRESENTATIVE MAKE AND MODEL NUMBER. IN THE EVENT THE HOOD SELECTED AND FURNISHED BY THE CONTRACTOR HAS DIFFERENT HOOD DATA, THE CONTRACTOR SHALL BE RESPONSIBLE FOR MAKING NECESSARY MODIFICATIONS TO THE DESIGN AND CONSTRUCTION WITHOUT ANY ADDITIONAL COST TO THE GOVERNMENT.
DESIGNER NOTE
1. BIOLOGICAL SAFETY CABINETS PROVIDED UNDER ARCHITECTURAL EQUIPMENT DRAWINGS.
2. FINAL DRAWING SIZE = 12 IN. WIDE

## SS230511-01
HVAC DESIGN DATA
DESIGN CONDITIONS | SUMMER |  |  |  |  | WINTER |  |  |  |  | LOWEST AVERAGE ANNUAL DEWPOINT
| TEMP |  | WET BULB TEMP |  | % HUMIDITY | TEMP |  | DEWPOINT TEMP |  | % HUMIDITY
| °F | [°C] | °F | [°C] |  | °F | [°C] | °F | [°C] |  | °F | [°C]
OUTDOOR DESIGN CONDITIONS | 96 | 35.6 | 77 | 25 | 46 | 2 | -16.7 | 0 | -17.8 | NA | -5 | -20.6
INDOOR AREA DESIGN CONDITIONS
OPERATING ROOMS | 66 | 18.9 | 56 | 13.3 | 55 | 80 | 26.7 | 45 | 7.2 | 30
PATIENT ROOM | 70 | 21.1 | 58 | 14.4 | 50 | 75 | 23.9 | 41 | 5 | 30
OFFICE | 75 | 23.9 | 62 | 16.7 | 50 | 70 | 21.1 | 37 | 2.8 | 30
EXAM ROOM | 75 | 23.9 | 62 | 16.7 | 50 | 70 | 21.1 | 37 | 2.8 | 30
PROCESSING ROOM | 70 | 21.1 | 58 | 14.4 | 50 | 75 | 23.9 | 41 | 5 | 30
WAREHOUSE | N/A | N/A | N/A | N/A | N/A | 68 | 20 | N/A | N/A | N/A
DESIGNER NOTES
1. USE LOWEST AVERAGE DEWPOINT PER NOAA FOR SIZING HUMIDIFERS.
2. SEE CHAPTER 7, HVAC DESIGN MANUAL.
3. INCLUDE A ROW FOR EACH ROOM TYPE, ABOUT 180.
4. FINAL DRAWING SIZE = 10 IN. WIDE

## SS230541-01
VIBRATION ISOLATION SCHEDULE | [7 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | EQUIPMENT AND/OR SERVICE | TYPE BASE | TYPE ISOLATOR | MIN STATIC DEFLECTION |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | IN | [mm]
5-VI1 | ROOF | 5-SF1 | B | S | 1.1 | 28 | ---
0
0
0
0
0
DESIGNER NOTES
1. REFER TO SELECTION GUIDE IN HVAC DESIGN MANUAL AND MANUFACTURER'S DATA FOR TYPE OF ISOLATOR AND MINIMUM STATIC DEFLECTION. LIST EQUIPMENT NOT REQUIRING ISOLATORS (PUMPS IN SEPARATE CHILLER BUILDING, COOLING TOWERS AT GRADE, PACKAGED CHILLER, ETC.) TO ENSURE EQUIPMENT WAS NOT OVERLOOKED. NOTE THAT PAD TYPE ISOLATORS FOR CENTRIFUGAL CHILLERS ARE SPECIFIED AND SUPPLIED BY THE CHILLER MANUFACTURER.
2. FINAL DRAWING SIZE = 10 IN. WIDE

## SS230911-01
BOILER PLANT · NATURAL GAS FLOWMETER SCHEDULE | [12 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | LINE PRESSSURE |  | ACCURATE FLOW RANGE |  | MIN ACCURACY (%) | DIFF PRESS AT MAX FLOW |  | GAS COMPANY BASE PRESS |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  | PSIG | [kPa] | CFH | [L/m] |  | IN | [mm] | PSIG | [kPa]
60-NGFM1 | BOILER PLANT |  |  | 0 |  | 0 |  |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  |  | 0 |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 12 IN. WIDE
UPDATED: 12/1/2017

## SS230911-02
BOILER PLANT · OIL FLOWMETER SCHEDULE | [14 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | OIL TYPE # | OIL VISCOSITY RANGE (SSU) | FLUID TEMP |  | LINE PRESSURE |  | ACCURATE FLOW RANGE |  | MIN ACCURACY [%] | DIFF PRESS AT MAX FLOW |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | °F | [°C] | PSIG | [kPa] | GPM | [L/s] |  | PSIG | [kPa]
60-OFM1 | BOILER PLANT | [6 empty] | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  | 0 |  |  | 0
[8 empty] | 0 |  | 0 |  |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 14 IN. WIDE
UPDATED: 12/1/2017

## SS230911-03
BOILER PLANT · WATER FLOWMETER SCHEDULE | [12 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | FLUID TEMP |  | LINE PRESSURE |  | ACCURATE FLOW RANGE |  | MIN ACCURACY [%] | DIFF PRESS AT MAX FLOW |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  | °F | [°C] | PSIG | [kPa] | GPM | [L/s] |  | PSIG | [kPa]
60-WFM1 | BOILER PLANT |  |  |  |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  | 0 |  |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 12 IN. WIDE
UPDATED: 12/1/2017

## SS230923-01
AIR FLOW MEASURING DEVICE SCHEDULE | [13 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | AIR FLOW |  |  |  | DUCT SIZE |  |  |  | APD |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  | MIN |  | MAX |  | WIDTH |  | HEIGHT
|  |  | CFM | [L/s] | CFM | [L/s] | IN | [mm] | IN | [mm] | IN | [mm]
1-AFMD1 | B1100 | 1-AHU1 | 2800 | 1300 | 4000 | 1900 | 48 | 1200 | 24 | 600 | 0.1 | 2.5 | MINIMUM OA DUCT
1-AFMD2 | B1100 | 1-AHU1 | 12000 | 5700 | 20000 | 9400 | 60 | 1500 | 40 | 1000 | 0.12 | 3 | MAIN SUPPLY AIR
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
DESIGNER NOTE
1. SCHEDULE ALL AIR FLOW MEASURING DEVICES.
2. FINAL DRAWING SIZE = 12 IN.

## SS230923-02
SMOKE AND COMBINATION FIRE/SMOKE DAMPER SCHEDULE | [8 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | FAN SYSTEM | SYSTEM AND/OR SERVICE | DUCT SIZE |  | DUCT PRESSURE CLASS |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  |  | IN | [mm] | IN WG | [Pa]
1-F/SDPR1 | 101, LOBBY | 1-SF1 | 1-AHU1 | 28 x 20 | [700 x 500] | 1 | 250 | COMBINATION F/S
1-SDPR1 | 150, MER | 1-SF1 | 1-AHU1 | 28 x 20 | [700 x 500] | 4 | 1000 | SMOKE DAMPER
0
0
0
0
0
0
0
0
DESIGNER NOTE
FINAL DRAWING SIZE = 10 IN. WIDE

## SS230923-03
HOISTWAY VENT DAMPER SCHEDULE | [9 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | ELEVATOR | LOCATION | HOISTWAY IDENTIFICATION | WIDTH |  | HEIGHT |  | WALL OR ROOF VENT | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  |  | IN | [mm] | IN | [mm]
1-HVD1 | SERVICE #1 | PENTHOUSE | 1-EV6 | 48 | 1200 | 24 | 600 | WALL | ---
[5 empty] | 0 |  | 0
[5 empty] | 0 |  | 0
[5 empty] | 0 |  | 0
[5 empty] | 0 |  | 0
[5 empty] | 0 |  | 0
[5 empty] | 0 |  | 0
[5 empty] | 0 |  | 0
[5 empty] | 0 |  | 0
[5 empty] | 0 |  | 0
[5 empty] | 0 |  | 0
[5 empty] | 0 |  | 0
[5 empty] | 0 |  | 0
[5 empty] | 0 |  | 0
DESIGNER NOTEs
1. LOUVERS (ARCHITECTURAL) AND DAMPERS ARE REQUIRED FOR ALL HOISTWAYS.
2. FINAL DRAWING SIZE = 10 IN. WIDE

## SS232111-01
BOILER PLANT · WATER FLOW CONTROL VALVE SCHEDULE | [19 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | MINIMUM FLOW COEFFICIENT [CV] | VALVE SIZE INCHES [MM] | MAXIMUM FLOW |  | DESIGN FLOW |  | MINIIMUM FLOW |  | WATER TEMP |  | MAX INLET PRESS |  | MIN INLET PRESS |  | MAX LEAKAGE AT SHUTOFF | FAILSAFE POSITION | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | GPM | [L/s] | GPM | [L/s] | GPM | [L/s] | °F | [°C] | PSIG | [kPa] | PSIG | [kPa]
60-WFCV1 | BOILER PLANT | BOILER 1 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 14 IN. WIDE
UPDATED: 12/1/2017

## SS232111-02
BOILER PLANT · BLOWOFF TANK WATER OUTLET TEMPERATURE CONTROL VALVE SCHEDULE | [14 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | MINIMUM FLOW COEFFICIENT [CV] | VALVE SIZE INCHES [MM] | MAXIMUM FLOW |  | DESIGN FLOW |  | MINIIMUM FLOW |  | MAX INLET PRESS |  | MAX LEAKAGE AT SHUTOFF | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | GPM | [L/s] | GPM | [L/s] | GPM | [L/s] | PSIG | [kPa]
60-BTCV1 | BOILER PLANT | BOILER 1 |  |  |  | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 12 IN. WIDE
UPDATED: 12/1/2017

## SS232111-03
BOILER PLANT · STEAM PRESSURE REDUCING VALVE SCHEDULE | [12 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | VALVE SIZE [MM] INCHES | REQUIRED CAPACITY |  | MAX FLOW WIDE OPEN VALVE |  | PRESSURE |  |  |  | REMARKS
[8 empty] | IN |  | OUT |  |  | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  |  | LBS/HR | [kg/HR] | LBS/HR | [kg/HR] | PSIG | [kPa] | PSIG | [kPa]
60-SPRV1 | BOILER PLANT |  |  |  | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0
DESIGNER NOTES
1. MUST BE LESS THAN OR EQUAL TO SAFETY VALVE CAPACITY.
2. STEAM IS DRY AND SATURATED.
3. FINAL DRAWING SIZE = 12 IN. WIDE
UPDATED: 12/1/2017

## SS232111-04
BOILER PLANT · STEAM TRAP SCHEDULE | [12 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | CAPACITY AT MIN DIFF PRESS |  | MIN DIFF PRESS |  | MIN INLET PRESS |  | TRAP TYPE | TRAP SIZE |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  | LBS/HR | [kg/HR] | PSI | [kPa] | PSI | [kPa] |  | IN | [mm]
60-ST1 | BOILER PLANT | HEADER |  | 0 |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 12 IN. WIDE
UPDATED: 12/1/2017

## SS232113-01
STEAM TO WATER HEAT EXCHANGER SCHEDULE | [26 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | WATER CONDITIONS | [7 empty] | STEAM PRESSURE |  |  |  | CONTROL VALVE |  |  |  |  | TRAP |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | FLOW |  | EWT |  | LWT |  | WPD |  | ENT CONTROL VALVE |  | ENT HEAT EXCHANGER | [6 empty] | TRAP # | SIZE [MM] INCHES | CAPACITY
[5 empty] | GPM | [L/s] | °F | [°C] | °F | [°C] | FT | [kPa] | PSIG | [kPa] | PSIG | [kPa] | Cv | SIZE [MM] | SIZE[IN] | LBS/HR | [kg/HR] |  |  | LBS/HR | [kg/HR]
1-SWHX1 | 0190 MER | PATIENT CARE | HEATING WATER | SHELL & TUBE | 200 | 13 | 158 | 70 | 180 | 82.2 | 9 | 27 | 30 | 210 | 18 | 120 |  |  |  | 2340 | 0 | 1-TP2 |  | 4680 | 2100 | ----
[6 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 16 IN. WIDE
UPDATED: 12/1/2017

## SS232113-02
LIQUID TO LIQUID HEAT EXCHANGER SCHEDULE | [22 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | OPERATING PRESSURE PSIG | HOT SIDE | [7 empty] | COLD SIDE | [7 empty] | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[6 empty] | FLOW |  | EWT |  | LWT |  | WPD |  | FLOW |  | EWT |  | LWT |  | WPD
[6 empty] | GPM | [L/s] | °F | [°C] | °F | [°C] | FT | [kPa] | GPM | [L/s] | °F | [°C] | °F | [°C] | FT | [kPa]
1-LLHX2 | 0190 MER | PATIENT CARE | HEATING WATER | PLATE & FRAME |  | 200 | 13 | 180 | 82.2 | 158 | 70 | 14 | 42 | 50 | 3.2 | 52 | 11.1 | 140 | 60 | 8 | 24 | -----
[7 empty] | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[7 empty] | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[7 empty] | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[7 empty] | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[7 empty] | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[7 empty] | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[7 empty] | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[7 empty] | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[7 empty] | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[7 empty] | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 16 IN. WIDE
UPDATED: 12/1/2017

## SS232113-03
EXPANSION TANK SCHEDULE | [26 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | TYPE | APPROX SYSTEM VOLUME |  | SYSTEM TEMPERATURE RANGE |  |  |  | INITIAL PRESSURE IN TANK |  | MAX OPERATING PRESSURE |  | FILL PRESSURE AT TANK |  |  |  | MIN VOLUME TANK |  | MIN BLADDER VOLUME |  | PIPE SIZE TO TANK |  | MAKE-UP WATER FILL SIZE |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[6 empty] | MIN |  | MAX | [5 empty] | RELIEF VALVE |  | AT TANK
|  |  |  | GAL | [L] | °F | [°C] | °F | [°C] | PSIG | [kPa] | PSIG | [kPa] | PSIG | [kPa] | PSIG | [kPa] | GAL | [L] | GAL | [L] | IN | [mm] | IN | [mm]
1-ET1 | 1090 MER | HEATING WATER | VERT DIAPHRAGM | 770 | 2900 | 60 | 15.6 | 180 | 82.2 | 10 | 69 | 70 | 480 | 80 | 550 | 70 | 480 | 56 | 210 | 23 | 87 | 1 | 25 | 0.75 | 19
[5 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 19 IN. WIDE
UPDATED: 12/1/2017

## SS232113-04
AIR SEPARATOR SCHEDULE | [11 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | TYPE | AIR SEPARATOR | [6 empty] | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  |  | SIZE IN |  | FLOW |  | WPD |  | BUILT-IN STRAINER REQ'D
|  |  |  | IN | [mm] | GPM | [L/s] | FT | [kPa]
1-AS1 | 01090 MER | HEATING WATER | FULL FLOW TANGENTIAL | 4 | 100 | 240 | 15 | 3.2 | 9.6 | YES | ---
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 12 IN. WIDE
UPDATED: 12/1/2017

## SS232123-01
PUMP SCHEDULE | [22 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | CIRCULATING FLUID | [9 empty] | MIN % EFF | ELECTRICAL MOTOR | [6 empty] | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | FLUID | FLOW |  | HEAD |  | NPSH AVAILABLE |  | TEMPERATURE |  | SP GR |  | NOMINAL POWER |  | PHASE | VOLT | MAX RPM | SPEED CONTROL | REMARKS
[6 empty] | GPM | [L/s] | FT | [kPa] | FT | [kPa] | °F | [°C] |  |  | HP | [kW]
1-P1 | 1220 MER | SURGERY | CONDENSER WATER | VERTICAL TURBINE | CONDENSER WATER | 380 | 24 | 65 | 1000 | 4.5 | 72 | 90 | 32.2 | 1 | 62 | 15 | 11 | 3 | 460 | 1750 | CONSTANT | ----
1-P2 | 1220 MER | SURGERY | CHILLED WATER | END SUCTION | CHILLED WATER | 255 | 16 | 46 | 730 | N/A | N/A | 42 | 5.6 | 1 | 68 | 7.5 | 5.6 | 3 | 460 | 1750 | VARIABLE | ----
1-P3 | 1090 MER | PATIENT CARE | HEATING WATER | END SUCTION | BUILDING HEATING WATER | 220 | 14 | 40 | 640 | N/A | N/A | 160 | 71.1 | 1 | 66 | 5 | 3.7 | 3 | 460 | 1750 | CONSTANT | ----
1-P4 | 1090 MER | PATIENT CARE | HEATING WATER, PREHEAT COIL | END SUCTION | BUILDING PREHEAT 20% PGW | 100 | 6.3 | 25 | 400 | N/A | N/A | 180 | 82.2 | 1.03 | 66 | 2 | 1.5 | 3 | 460 | 1750 | CONSTANT | ----
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0
DESIGNER NOTES
1. ANTIFREEZE FLUID IS USUALLY PROPYLENE GLYCOL WATER (PGW). ADJUST FLOW, HEAD, AND POWER FOR FLUID PUMPED, EXCEPT SIZE MOTORS FOR HOT FLUIDS ON COLD CONDITIONS.
2. FINAL DRAWING SIZE = 19 IN. WIDE

## SS232213-01
STEAM HUMIDIFER SCHEDULE | [25 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SEVICE | HUMIDIFIER TYPE | AIR FLOW |  | # OF MANIFOLDS | EAT |  |  |  | LAT |  |  | SOURCE | STEAM | [5 empty] | CONTROL TYPE | TRAP |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[7 empty] | Db |  | DEWPOINT |  | %RH | DEWPOINT |  |  | PRESS ENT VALVE |  | PRESS ENT HEATER |  | FLOW |  |  | MARK | CAPACITY
|  |  |  | CFM | [L/s] |  | °F | [°C] | °F | [°C] |  | °F | [°C] |  | PSIG | [kPa] | PSIG | [kPa] | LBS/HR | [kg/HR] |  |  | LBS/HR | [kg/HR]
1-SH1 | 0190 MER | 1-AHU1 | UNIT-MOUNTED DISPERSION TUBE | 10000 | 4700 | 3 | 75 | 23.9 | 10 | -12.2 |  | 45 | 7.2 | CLEAN STEAM | 15 | 100 | 8 | 55 | 250 | 110 | C-1 | 1-TP7 | 500 | 230
1-SH1 | 0190 MER | 1-AHU-2 | UNIT-MOUNTED DISPERSION TUBE | 10000 | 4700 | 3 | 55 | 12.8 | 18 | -7.8 |  | 47 | 8.3 | CLEAN STEAM | 15 | 100 | 8 | 55 | 230 | 100 | C-1 | 1-TP8 | 460 | 210
3-SH1 | 0190 MER | 1-TU-1 | TERMINAL UNIT | 2000 | 940 | 1 | 55 | 12.8 | 45 | 7.2 |  | 53 | 11.7 | CLEAN STEAM | 15 | 100 | 8 | 55 | 24 | 11 | C-2 | 1-TP9 | 50 | 23
[5 empty] | 0 | [10 empty] | 0 |  | 0 |  | 0 |  |  |  | 0
[5 empty] | 0 | [10 empty] | 0 |  | 0 |  | 0 |  |  |  | 0
[5 empty] | 0 | [10 empty] | 0 |  | 0 |  | 0 |  |  |  | 0
[5 empty] | 0 | [10 empty] | 0 |  | 0 |  | 0 |  |  |  | 0
[5 empty] | 0 | [10 empty] | 0 |  | 0 |  | 0 |  |  |  | 0
[5 empty] | 0 | [10 empty] | 0 |  | 0 |  | 0 |  |  |  | 0
[5 empty] | 0 | [10 empty] | 0 |  | 0 |  | 0 |  |  |  | 0
DESIGNER NOTES
1. TRAP ONLY HANDLES CONDENSATE FROM PIPING AND MANIFOLD JACKET.
2. SIZE HUMIDIFIER ON LOWEST ANNUAL DEWPOINT OBTAINED FROM NOAA.
3. MAX HUMIDIFER LOAD CAN OCCUR IN THE COOLING SEASON, I.E., ARIZONA, NEVADA.
4. HUMIDIFIER PROVIDED STEAM FROM CLEAN STEAM GENERATOR.
5. FINAL DRAWING = 20 IN. WIDE
UPDATED: 12/1/2017

## SS232213-02
STEAM PRESSURE RELIEF VALVE SCHEDULE | [9 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | TEMPERATURE |  | MINIMUM CAPACITY |  | SET PRESSURE |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  | °F | [°C] | LBS/HR | [kg/HR] | PSIG | [kPa]
1-SV1 | 01090 MER | STEAM PRV STATION | 287 | 140 | 4900 | 2200 | 40 | 280 | ----
|  |  |  | -18 |  | 0 |  | 0
|  |  |  | -18 |  | 0 |  | 0
|  |  |  | -18 |  | 0 |  | 0
|  |  |  | -18 |  | 0 |  | 0
|  |  |  | -18 |  | 0 |  | 0
|  |  |  | -18 |  | 0 |  | 0
|  |  |  | -18 |  | 0 |  | 0
|  |  |  | -18 |  | 0 |  | 0
DESIGNER NOTE
1. USE DESIGN LOAD FOR REQUIRED CAPACITY. THE MAXIMUM LOAD IS THE CATALOG RATING OF THE PRESSURE REGULATING VALVE SELECTED FOR THE DESIGN LOAD. SIZE THE BYPASS ACCORDING TO NATIONAL BOARD INSPECTION CODE OF THE NATIONAL BOARD OF BOILER AND PRESSURE VESSEL INSPECTORS.
2. FINAL DRAWING SIZE = 10 IN. WIDE
UPDATED: 12/1/2017

## SS232213-03
BUILDING · STEAM TRAP SCHEDULE | [12 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | CAPACITY AT MIN DIFF PRESS |  | MIN DIFF PRESS |  | MIN INLET PRESS |  | TRAP TYPE | TRAP SIZE |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  | LBS/HR | [kg/HR] | PSI | [kPa] | PSI | [kPa] |  | IN | [mm]
60-ST1 | BOILER PLANT | HEADER |  | 0 |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 12 IN. WIDE
UPDATED: 12/1/2017

## SS232213-04
BUILDING · STEAM PRESSURE REDUCING VALVE SCHEDULE | [12 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | VALVE SIZE [MM] INCHES | REQUIRED CAPACITY |  | MAX FLOW WIDE OPEN VALVE |  | PRESSURE |  |  |  | REMARKS
[8 empty] | IN |  | OUT |  |  | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  |  | LBS/HR | [kg/HR] | LBS/HR | [kg/HR] | PSIG | [kPa] | PSIG | [kPa]
60-SPRV1 | BOILER PLANT |  |  |  | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0
DESIGNER NOTES
1. MUST BE LESS THAN OR EQUAL TO SAFETY VALVE CAPACITY.
2. STEAM IS DRY AND SATURATED.
3. FINAL DRAWING SIZE = 12 IN. WIDE
UPDATED: 12/1/2017

## SS232213-05
CLEAN STEAM GENERATOR SCHEDULE | [28 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | SOURCE OF MAKEUP | WATER CONDITIONS |  |  |  | PRODUCED STEAM FLOW |  | PRODUCED STEAM PRESS |  | STEAM PRESSURE |  |  |  | CONTROL VALVE |  |  |  |  | TRAP |  |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[6 empty] | FLOW |  | EWT | [5 empty] | ENT CONTROL VALVE |  | ENT HEAT EXCHANGER | [6 empty] | TRAP # | # TRAPS | SIZE [MM] INCHES | CAPACITY EACH
[6 empty] | GPM | [L/s] | °F | [°C] | LBS/HR | kg/HR | PSIG | [kPa] | PSIG | [kPa] | PSIG | [kPa] | Cv | SIZE [MM] | SIZE[IN] | LBS/HR | [kg/HR] |  |  |  | LBS/HR | [kg/HR]
1-SSHX3 | 0190 MER | ICU | HUMIDIFICATION | STEAM-STEAM | RO | 10 | 0.6 | 50 | 10 | 5000 | 2300 | 15 | 100 | 60 | 410 | 45 | 310 |  |  |  | 5300 | 0 | 1-TP7, 1-TP8, 1-TP9 | 3 |  | 4000 | 1800 | ---
[7 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
[7 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
[7 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
[7 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
[7 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
[7 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
[7 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
[7 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
[7 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0 |  |  |  |  | 0
DESIGNER NOTE
FINAL DRAWING = 20 IN. WIDE
UPDATED: 12/1/2017
ADDED COLUMN

## SS232223-01
STEAM CONDENSATE PUMP SCHEDULE | [15 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | TYPE UNIT | FLOW EACH PUMP |  | DISCHARGE PRESSURE |  | MIN RECEIVER SIZE |  | MOTOR |  |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[10 empty] | NOMINAL POWER EACH |  | PHASE | VOLT | RPM
|  |  |  | GPM | [L/s] | PSIG | [kPa] | GAL | [L] | HP | [W]
30-CP1 | MECH ROOM, 1-B106 | BLDG STEAM | DUPLEX | 15 | 0.9 | 20 | 140 | 30 | 110 | 0.5 | 370 | 1 | 120 | 1750 | ----
[5 empty] | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0
NOTE
1. PROVIDE NON-RESETTABLE HOUR METERS TO LOG RUN TIME OF EACH PUMP.
DESIGNER NOTE
1. FINAL DRAWING = 12 IN. WIDE
2. FOR DUPLEX PUMP, STATE IF REDUNDANT (ONLY ONE PUMP RUNS) OR IF PUMPS ARE STAGED AND THEN ALLOWED TO RUN AT THE SAME TIME TO MEET LOADS.
UPDATED: 12/1/2017

## SS232223-PRESS POWERED PUMP
PRESSURE POWERED CONDENSATE PUMP SCHEDULE | [13 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | TYPE UNIT | FILLING HEAD [MM] INCHES | MOTIVE STEAM PRESSURE |  | CONDENSATE FLOW |  | DISCHARGE PRESSURE |  | MIN RECEIVER SIZE |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | PSIG | [kPa] | GPM | [L/s] | PSIG | [kPa] | GAL | [L]
30-CP1 | MECH ROOM, 1-B106 | BLDG STEAM | PACKAGED PRE-PIPED | 305 [12] | 50 | 350 | 15 | 0.9 | 20 | 140 | 30 | 110 | ----
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0 |  | 0
NOTE
DESIGNER NOTE
FINAL DRAWING = 12 IN. WIDE
UPDATED: 12/1/2017

## SS232500-01
WATER FILTER SCHEDULE (SIDE STREAM) | [11 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | TYPE | SIZE | CAPACITY |  | MAX WPD |  | AUTOMATIC VALVE PRESSURE RANGE |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | GPM | [L/s] | FT | [kPa] | PSIG | [kPa]
1-WF1 | 118, MER | CHILLED WATER |  |  | 100 | 6.3 | 8 | 24 | 4 to 60 | [ 28 to 410 ] | ----
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
DESIGNER NOTES
1. PROVIDE WATER FILTERS FOR EACH CHILLED WATER, HEATING HOT WATER, AND GLYCOL WATER SYSTEM. AUTOMATIC VALVE PRESSURE RANGE SHOULD APPROXIMATE PUMP SHUTOFF HEAD.
2. SELECT FILTER FLOW RATE EQUAL TO 5% OF TOTAL SYSTEM PUMPING CAPACITY.
3. FINAL DRAWING = 12 IN. WIDE

## SS232500-02
SOLID SEPARATOR SCHEDULE (SIDE STREAM) | [14 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | TYPE | SIZE |  | CAPACITY |  | MAX WPD |  | AUTOMATIC VALVE PRESSURE RANGE |  | SIDE STREAM | PUMP # | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  |  | IN | [mm] | GPM | [L/S] | FT | [kPa] | PSIG | [kPa]
1-SSR1 | PLANT | CONDENSER | CENT | 4 | 100 | 200 | 13 | 10 | 30 | 4 to 60 | [ 28 to 410 ] | YES | NA | ----
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0
DESIGNER NOTES
1. PROVIDE EITHER A COMMON SIDESTREAM SOLID SEPARATOR WITH PUMP OR A DEDICATED SEPARATOR FOR EACH CONDENSER WATER SYSTEM.
2. INCREASE CONDENSER WATER PUMP CAPACITY 5%-8% FOR A DEDICATED SIDESTREAM SEPARATOR.
3. FINAL DRAWING = 12 IN. WIDE

## SS233100-01
INTAKE/EXHAUST HOOD SCHEDULE | [12 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | TYPE | APPLICATION | THROAT SIZE |  | AIR FLOW |  | APD |  | DAMPER TYPE | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | IN | [mm] | CFM | [L/s] | IN | [Pa]
1-EH1 | ROOF | 1-AHU1 | INTAKE | DUCTED | 24 x 18 | [ 600 x 450 ] | 1700 | 800 | 0.18 | 45 | BACKDRAFT | ----
22-EH2 | ROOF | WAREHOUSE RELIEF | EXHAUST | GRAVITY | 20 x 20 | [ 480 x 480 ] | 2000 | 940 | 0.15 | 38 | BACKDRAFT | -----
[8 empty] | 0 |  | 0
[8 empty] | 0 |  | 0
[8 empty] | 0 |  | 0
[8 empty] | 0 |  | 0
[8 empty] | 0 |  | 0
[8 empty] | 0 |  | 0
[8 empty] | 0 |  | 0
[8 empty] | 0 |  | 0
DESIGNER NOTE
FINAL DRAWING = 12 IN. WIDE

## SS233100-02
SOUND ATTENUATING DEVICE SCHEDULE | [20 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | TYPE | AIRFLOW |  | APD |  | INLET SIZE |  | LENGTH |  | DYNAMIC INSERTION LOSS DB OCTAVE BAND AND MID-FREQUENCY [CPS] | [7 empty] | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[12 empty] | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
|  |  |  | CFM | [L/s] | IN WG | [Pa] | IN | [mm] | IN | [mm] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1-SAD1 | 190 | 1-AHU1 | CIRCULAR | 9500 | 4500 | 0.3 | 75 | 36 | 240000 | 36 | 900 | N/A | 8 | 12 | 16 | 24 | 30 | 24 | 20 | ----
1-SAD2 | 190 | 1-AHU2 | RECTANGULAR | 9500 | 4500 | 0.3 | 75 | 36 x 36 | [900 x 900] | 48 | 1200 | N/A | 6 | 10 | 13 | 21 | 25 | 21 | 15 | ----
[5 empty] | 0 |  | 0 |  |  |  | 0
[5 empty] | 0 |  | 0 |  |  |  | 0
[5 empty] | 0 |  | 0 |  |  |  | 0
[5 empty] | 0 |  | 0 |  |  |  | 0
[5 empty] | 0 |  | 0 |  |  |  | 0
[5 empty] | 0 |  | 0 |  |  |  | 0
[5 empty] | 0 |  | 0 |  |  |  | 0
[5 empty] | 0 |  | 0 |  |  |  | 0
NOTE
IN THE INLET SIZE COLUMN, WHEN ONE VALUE IS INDICATED, THE DUCT IS A ROUND DUCT. IF SIZE IS INDICATED AS ##" x ##," THE DUCT IS A RECTANGULAR DUCT WITH SPECIFICATIONS OF "DUCT WIDTH" BY "DUCT DEPTH."
DESIGNER NOTE
FINAL DRAWING SIZE = 16 IN. WIDE

## SS233100-03
CANOPY HOOD SCHEDULE | [10 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | HOOD TYPE | HOOD SIZE |  | EXHAUST |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[6 empty] | AIR FLOW |  | APD HOOD ONLY
|  |  |  | IN | [mm] | CFM | [L/s] | IN WG | [Pa]
1-HD4 | ROOM 114 | EXHAUST SYSTEM 1-EF2 | A | 48 x 24 | [1200 x 600] | 800 | 380 | 0.3 | 75 | -----
1-HD10 | ROOM 110 | EXHAUST SYSTEM 1-EF10 | B | 60 x 30 | [1500 x 750] | 1250 | 590 | 0.3 | 75 | -----
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
[7 empty] | 0 |  | 0
DESIGNER NOTE
1. TYPE A AND B CANOPY HOODS ARE FURNISHED BY DIVISION 23 00 00.
2. FINAL DRAWING SIZE = 10 IN. WIDE

## SS233400-01
FAN SCHEDULE | [25 empty] | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | BELT ID | SHEAVE ID | PM NO
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | AIR FLOW |  | TSP |  | FAN | [8 empty] | MOTOR ELECTRICAL | [6 empty] | CONTROL SEQUENCE | REMARKS
[8 empty] | TYPE | WHEEL | CLASS | ARRANGEMENT, ROTATION, AND DISCHARGE | DIAMETER |  | MIN % EFF | DRIVE | FAN MAX RPM | NOMINAL POWER |  |  | PHASE | VOLT | RPM | SPEED CONTROL
|  |  |  | CFM | [L/s] | IN | [Pa] |  |  |  |  | IN | [mm] |  |  |  | BHP | HP | [kW]
1-SF1 | B309 | 3 NORTH | 1-AHU1 | 20000 | 9400 | 4.7 | 1200 | DOUBLE WIDTH DOUBLE INLET | AIRFOIL | II | ARR 3, CW ROTATION, TH DISCHARGE | 28 | 700 | 75% | BELT | 1314 | 20.3 | 25 | 19 | 3 | 460 | 1750 | VARIABLE |  | ---
1-SF2 | B409 | 4 NORTH | 1-AHU2 | 17500 | 8300 | 4.3 | 1100 | DOUBLE WIDTH DOUBLE INLET | AIRFOIL | II | ARR 3, CW ROTATION, TH DISCHARGE | 28 | 700 | 75% | BELT | 1278 | 16.6 | 20 | 15 | 3 | 460 | 1750 | VARIABLE |  | ---
1-SF3 | B509 | 5 NORTH | 1-AHU3 | 16000 | 7600 | 3.8 | 950 | DOUBLE WIDTH DOUBLE INLET | AIRFOIL | I | ARR 3, CW ROTATION, TH DISCHARGE | 25 | 630 | 71% | BELT | 1454 | 16 | 20 | 15 | 3 | 460 | 1750 | VARIABLE |  | ---
1-RF1 | B309 | 3 NORTH | 1-AHU1 | 14800 | 7000 | 1.2 | 300 | VANEAXIAL | N/A | I | ARR 9, INLINE, HORIZ. DISCHARGE | 36 | 900 | 52% | DIRECT | 1169 | 6.74 | 7.5 | 5.6 | 3 | 460 | 1750 | VARIABLE |  | ----
1-RF2 | B409 | 4 NORTH | 1-AHU2 | 11100 | 5200 | 1.1 | 280 | VANEAXIAL | N/A | I | ARR 9, INLINE, HORIZ. DISCHARGE | 30 | 750 | 69% | DIRECT | 1243 | 3.68 | 5 | 3.7 | 3 | 460 | 1750 | VARIABLE |  | ----
1-RF3 | B509 | 5 NORTH | 1-AHU3 | 9600 | 4500 | 1.2 | 300 | VANEAXIAL | N/A | I | ARR 9, INLINE, HORIZ. DISCHARGE | 30 | 750 | 61% | DIRECT | 1300 | 3.63 | 5 | 3.7 | 3 | 460 | 1750 | VARIABLE |  | ----
1-EF1 | ROOF | 3 & 4 NORTH | TOILET EXHAUST | 4500 | 2100 | 1.4 | 350 | UPBLAST CENTRIFUGAL | BIW | I | N/A | 30 | 750 | 54% | BELT | 1229 | 1.8 | 2 | 1.5 | 3 | 460 | 1750 | CONSTANT |  | ----
1-EF2 | ROOF | 4 NORTH | LAB EXHAUST | 7500 | 3500 | 2.4 | 600 | UTILITY | BIW | I | ARR 10, CW ROTATION, UPBLAST | 24 | 600 | 71% | BELT | 1249 | 4.23 | 5 | 3.7 | 3 | 460 | 1750 | CONSTANT |  | ----
1-EF3 | ROOF | 5 NORTH | TOILET EXHAUST | 1600 | 760 | 1.3 | 330 | UPBLAST CENTRIFUGAL | BIW | I | N/A | 24 | 600 | 54% | BELT | 1330 | 0.65 | 1 | 0.7 | 3 | 460 | 1750 | CONSTANT |  | ----
[5 empty] | 0 |  | 0 | [5 empty] | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 | [5 empty] | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 | [5 empty] | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 | [5 empty] | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 | [5 empty] | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 | [5 empty] | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 | [5 empty] | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 | [5 empty] | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 | [5 empty] | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 | [5 empty] | 0 | [5 empty] | 0
NOTE
ALL SELECTIONS ARE BASED ON AN ALTITUDE OF ___.
DESIGNER NOTES
1. INDICATE SITE ALTITUDE.
2. FINAL DRAWING SIZE = 19 IN. WIDE

## SS233600-01
AIR TERMINAL UNIT SIZING SCHEDULE
SIZE | MIN ALLOWABLE AIR FLOW |  | MAX ALLOWABLE AIR FLOW |  | DUCT INLET SIZE |  | MAX APD |  | MAXIMUM SOUND POWER LEVEL (Re: 10 -12 WATTS) FOR BOX DISCHARGE AT MAXIMUM INLET DUCT STATIC | [5 empty] | HOT WATER HEATING COIL | [9 empty] | REMARKS
[9 empty] | OCTAVE BANDS | [5 empty] | EAT |  | EWT |  | FLOW |  | MAX WPD |  | PIPE RUNOUT SIZE TO COIL
| CFM | [L/s] | CFM | [L/s] | IN | [mm] | IN WG | [Pa] | 2 | 3 | 4 | 5 | 6 | 7 | °F | [°C] | °F | [°C] | GPM | [L/m] | FT | [kPa] | IN | [mm]
A | 60 | 28 | 170 | 80 | 4 | 100 | 0.4 | 100 | 69 | 65 | 58 | 52 | 51 | 47 | 55 | 13 | 140 | 60 | 0.5 | 1.9 | 3 | 9 | 0.75 | 19 | ----
B | 90 | 42 | 260 | 120 | 5 | 130 | 0.4 | 100 | 69 | 63 | 59 | 52 | 51 | 47 | 55 | 13 | 140 | 60 | 0.5 | 1.9 | 3 | 9 | 0.75 | 19 | ----
C | 130 | 61 | 380 | 180 | 6 | 150 | 0.4 | 100 | 69 | 67 | 61 | 55 | 52 | 49 | 55 | 13 | 140 | 60 | 0.7 | 2.7 | 4 | 12 | 0.75 | 19 | ----
D | 160 | 76 | 490 | 230 | 7 | 180 | 0.4 | 100 | 70 | 68 | 63 | 57 | 53 | 49 | 55 | 13 | 140 | 60 | 0.7 | 2.7 | 4 | 12 | 0.75 | 19 | ----
E | 230 | 110 | 680 | 320 | 8 | 200 | 0.4 | 100 | 71 | 68 | 59 | 53 | 51 | 47 | 55 | 13 | 140 | 60 | 1 | 3.8 | 3 | 9 | 0.75 | 19 | ----
F | 270 | 130 | 790 | 370 | 9 | 230 | 0.4 | 100 | 71 | 69 | 60 | 54 | 51 | 47 | 55 | 13 | 140 | 60 | 1.5 | 5.7 | 4 | 12 | 0.75 | 19 | ----
G | 350 | 170 | 1050 | 500 | 10 | 250 | 0.4 | 100 | 74 | 68 | 61 | 57 | 54 | 52 | 55 | 13 | 140 | 60 | 1.5 | 5.7 | 4 | 12 | 0.75 | 19 | ----
H | 500 | 240 | 1500 | 710 | 12 | 300 | 0.4 | 100 | 73 | 69 | 64 | 59 | 57 | 53 | 55 | 13 | 140 | 60 | 2.5 | 9.5 | 3 | 9 | 0.75 | 19 | ----
I | 750 | 350 | 2250 | 1100 | 14 | 350 | 0.4 | 100 | 73 | 68 | 65 | 61 | 61 | 59 | 55 | 13 | 140 | 60 | 3.5 | 13 | 4 | 12 | 0.75 | 19 | ----
J | 1000 | 470 | 3000 | 1400 | 16 | 400 | 0.4 | 100 | 73 | 68 | 66 | 60 | 58 | 55 | 55 | 13 | 140 | 60 | 4.5 | 17 | 4 | 12 | 1 | 25 | ----
NOTES
1. INLET STATIC BASED ON ARI 885-98.
2. THIS SCHEDULE IS USED WITH THE TERMINAL UNIT SCHEDULE.
3. CONTROL SEQUENCE SHALL BE AS INDICATED ON THE AIR TERMINAL UNIT SCHEDULE.
4. PROVIDE SOUND ATTENUATION AFTER-SECTION AS REQUIRED TO MEET ROOM NC LEVEL.
DESIGNER NOTE
1. AIR TERMINAL UNIT SELECTION IS BASED UPON A MAXIMUM UNIT DISCHARGE NOISE CRITERIA (NC) VALUE OF 27. UNIT DISCHARGE SOUND POWER LEVELS ARE BASED UPON A 1.55 IN W.G. [386 Pa] INLET STATIC PRESSURE. THE DESIGNER SHALL DESIGN THE DUCT DISTRIBUTION SYSTEM IN SUCH A WAY THAT INLET STATIC PRESSURE DOES NOT EXCEED 1.76 IN [44 mm]. ADDITIONAL SOUND ATTENUATION DOWNSTREAM OF AIR TERMINAL UNIT WILL BE REQUIRED IF ROOM NOISE CRITERIA VALUE MUST BE BELOW 30.
2. FINAL DRAWING SIZE = 16 IN. WIDE.

## SS233600-02
SINGLE DUCT AIR TERMINAL UNIT SCHEDULE | [16 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR ROOM SERVED | SYSTEM AIR HANDLING | SIZE | AIR FLOW |  |  |  | ADDITIONAL SOUND ATTUNATION REQUIRED | CONTROL TYPE | CONTROL SEQUENCE | REHEAT |  |  | PERIMETER SUPPLEMENTAL HEAT LINK | REMARKS | PM NO
[5 empty] | MAX |  | MIN
[5 empty] | CFM | [L/s] | CFM | [L/s] |  |  |  | HW | ELEC | NONE
1-TU-7-1 | 1100 | 1100B | 1-AHU7 | G | 850 | 400 | 450 | 210 | NONE | VAV | 5 DEGREE DEADBAND |  |  |  | RADIANT CEILING PANEL | ----
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
DESIGNER NOTES
1. REFER TO AIR TERMINAL UNIT SIZING SCHEDULE FOR ADDITIONAL INFORMATION.
2. DENOTE IN COLUMN CALLED "PERIMETER SUPPLEMENTAL HEAT" WHETHER THE AIR TERMINAL UNIT IS LINKED TO RADIANT CEILING PANELS (RCP), MISCELLANEOUS HEAT (SUCH AS FIN TUBE RADIATORS), OR NONE.
3. SCHEDULE ALL TERMINAL UNITS.
4. FINAL DRAWING SIZE = 16 IN. WIDE

## SS233600-03
AIR FLOW CONTROL VALVE SCHEDULE | [15 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | TYPE | SIZE |  | DESIGN AIR FLOW |  | MAX AIR FLOW |  | APD AT MAX AIR FLOW |  | CONTROL TYPE | CONNECT TO ECC | APPLICATION | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  |  | IN | [mm] | CFM | [L/s] | CFM | [L/s] | IN WG | [Pa]
1-AFCV7 | C1107 | 1-AHU2 | CV | 12 | 300 | 1250 | 590 | 1250 | 590 | 0.4 | 100 |  |  | ICU | ----
1-AFCV8 | C1107 | 1-AHU2 | VAV | 10 | 250 | 1000 | 470 | 630 | 300 | 0.4 | 100 |  |  | LAB
[5 empty] | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 14 IN.WIDE

## SS233700-01
AIR DEVICE SCHEDULE (SUPPLY) | [16 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | TYPE | AIR FLOW |  |  |  | MAX APD |  | MOUNTING | PANEL/FRAME SIZE |  | NECK SIZE |  | NC | DAMPER | FINISH | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  | MIN |  | MAX |  |  |  |  | IN x IN | [mm x mm] | IN | [mm ]
|  | CFM | [L/s] | CFM | [L/s] | IN WG | [Pa]
SD-11 | LOUVERED FACE | 40 | 19 | 160 | 76 | 0.08 | 20 | CEILING | 24 x 24 | [ 600 x 600 ] | 6 ø | [152 ø] | 19 | NONE | WHITE | ----
SD-12 | LOUVERED FACE | 70 | 33 | 280 | 130 | 0.1 | 25 | CEILING | 24 x 24 | [ 600 x 600 ] | 8 ø | [203 ø] | 23 | NONE | WHITE | -----
SD-13 | LOUVERED FACE | 110 | 52 | 380 | 180 | 0.09 | 23 | CEILING | 24 x 24 | [ 600 x 600 ] | 10 ø | [254 ø] | 22 | NONE | WHITE | -----
SD-14 | LOUVERED FACE | 160 | 76 | 470 | 220 | 0.08 | 20 | CEILING | 24 x 24 | [ 600 x 600 ] | 12 ø | [305 ø ] | 19 | NONE | WHITE | -----
SD-15 | LOUVERED FACE | 220 | 100 | 640 | 300 | 0.09 | 23 | CEILING | 24 x 24 | [ 600 x 600 ] | 14 ø | [356 ø ] | 21 | NONE | WHITE | -----
SD-16 | LOUVERED FACE | 250 | 120 | 740 | 350 | 0.1 | 25 | CEILING | 24 x 24 | [ 600 x 600 ] | 16 ø | [406 ø ] | 22 | NONE | WHITE | -----
SD-21 | PERFORATED | 60 | 28 | 180 | 85 | 0.1 | 25 | CEILING | 24 x 24 | [ 600 x 600 ] | 6 ø | [152 ø ] | 25 | NONE | WHITE | -----
SD-22 | PERFORATED | 110 | 52 | 320 | 150 | 0.1 | 25 | CEILING | 24 x 24 | [ 600 x 600 ] | 8 ø | [203 ø ] | 30 | NONE | WHITE | -----
SD-23 | PERFORATED | 160 | 76 | 450 | 210 | 0.1 | 25 | CEILING | 24 x 24 | [ 600 x 600 ] | 10 ø | [254 ø ] | 33 | NONE | WHITE | -----
SD-24 | PERFORATED | 240 | 110 | 700 | 330 | 0.1 | 25 | CEILING | 24 x 24 | [ 600 x 600 ] | 12 ø | [305 ø ] | 36 | NONE | WHITE | -----
SD-25 | PERFORATED | 220 | 100 | 950 | 450 | 0.1 | 25 | CEILING | 24 x 24 | [ 600 x 600 ] | 14 ø | [356 ø ] | 38 | NONE | WHITE | -----
SD-26 | PERFORATED | 280 | 130 | 1200 | 570 | 0.1 | 25 | CEILING | 24 x 24 | [ 600 x 600 ] | 16 ø | [406 ø ] | 41 | NONE | WHITE | -----
SD-41 | ROUND | 110 | 52 | 500 | 240 | 0.08 | 20 | DUCT MOUNTED | 18 ø | [457 ø ] | 10 ø | [254 ø ] | 41 | NONE | WHITE | -----
SD-42 | ROUND | 160 | 76 | 760 | 360 | 0.08 | 20 | DUCT MOUNTED | 22 ø | [559 ø ] | 12 ø | [305 ø ] | 42 | NONE | WHITE | -----
SD-43 | ROUND | 220 | 100 | 1000 | 470 | 0.08 | 20 | DUCT MOUNTED | 26 ø | [660 ø ] | 14 ø | [356 ø ] | 43 | NONE | WHITE | -----
SD-44 | ROUND | 280 | 130 | 1300 | 610 | 0.08 | 20 | DUCT MOUNTED | 29 ø | [737 ø ] | 16 ø | [406 ø ] | 44 | NONE | WHITE | -----
SD-45 | ROUND | 350 | 170 | 1500 | 710 | 0.08 | 20 | DUCT MOUNTED | 33 ø | [838 ø ] | 18 ø | [457 ø ] | 42 | NONE | WHITE | -----
SD-46 | ROUND | 440 | 210 | 2000 | 940 | 0.08 | 20 | DUCT MOUNTED | 36 ø | [914 ø ] | 20 ø | [508 ø ] | 45 | NONE | WHITE | -----
SD-51 | SUPPLY REGISTER | 80 | 38 | 120 | 57 | 0.1 | 25 | WALL | 8 x 8 | [203 x 203] | 6 x 6 | [152 x 152] | 25 | OBD | WHITE | -----
SD-52 | SUPPLY REGISTER | 80 | 38 | 160 | 76 | 0.09 | 23 | WALL | 12 x 8 | [305 x 203] | 10 x 6 | [254 x 152] | 25 | OBD | WHITE | -----
SD-53 | SUPPLY REGISTER | 130 | 61 | 350 | 170 | 0.08 | 20 | WALL | 14 x 10 | [356 x 254] | 12 x 8 | [305 x 203] | 26 | OBD | WHITE | -----
SD-54 | SUPPLY REGISTER | 200 | 94 | 500 | 240 | 0.1 | 25 | WALL | 14 x 12 | [356 x 305] | 12 x 10 | [305 x 254] | 26 | OBD | WHITE | -----
SD-55 | SUPPLY REGISTER | 400 | 190 | 700 | 330 | 0.08 | 20 | WALL | 18 x 12 | [508 x 305] | 18 x 10 | [457 x 254] | 26 | OBD | WHITE | -----
SD-56 | SUPPLY REGISTER | 360 | 170 | 700 | 330 | 0.07 | 18 | WALL | 18 x 18 | [457 x 457] | 16 x 16 | [406 x 406] | 27 | OBD | WHITE | -----
SD-57 | SUPPLY REGISTER | 560 | 260 | 1100 | 520 | 0.07 | 18 | WALL | 22 x 22 | [560 x 560] | 20 x 20 | [508 x 508] | 28 | OBD | WHITE | -----
SD-58 | SUPPLY REGISTER | 1250 | 590 | 3000 | 1400 | 0.1 | 25 | WALL | 32 x 32 | [813 x 813] | 30 x 30 | [762 x 762] | 36 | OBD | WHITE | -----
SD-61 | DRUM LOUVER | 100 | 47 | 200 | 94 | 0.09 | 23 | DUCT MOUNTED | 12 x 8 | [305 x 203] | 10 x 6 | [254 x 152] | 19 | NONE | WHITE | -----
SD-62 | DRUM LOUVER | 80 | 38 | 150 | 71 | 0.09 | 23 | DUCT MOUNTED | 14 x 6 | [356 x 152] | 12 x 4 | [305 x 102] | 15 | NONE | WHITE | -----
SD-63 | DRUM LOUVER | 150 | 71 | 300 | 140 | 0.09 | 23 | DUCT MOUNTED | 16 x 8 | [406 x 203] | 14 x 6 | [356 x 152] | 18 | NONE | WHITE | -----
SD-64 | DRUM LOUVER | 290 | 140 | 600 | 280 | 0.09 | 23 | DUCT MOUNTED | 22 x 10 | [560 x 254] | 20 x 8 | [508 x 203] | 21 | NONE | WHITE | -----
SD-65 | DRUM LOUVER | 450 | 210 | 900 | 420 | 0.09 | 23 | DUCT MOUNTED | 22 x 14 | [560 x 2356] | 20 x 12 | [508 x 305] | 23 | NONE | WHITE | -----
SD-66 | DRUM LOUVER | 670 | 320 | 1300 | 610 | 0.09 | 23 | DUCT MOUNTED | 32 x 14 | [813 x 356] | 30 x 12 | [762 x 305] | 25 | NONE | WHITE | -----
SD-67 | DRUM LOUVER | 550 | 260 | 1650 | 780 | 0.09 | 23 | DUCT MOUNTED | 38 x 14 | [965 x 356] | 36 x 12 | [914 x 305] | 25 | NONE | WHITE | -----
NOTES
1. SEE FLOOR PLAN FOR THROW PATTERN.
2. SEE DETAIL FOR DAMPER IN BRANCH DUCT SERVING EACH DIFFUSER.
3. PROVIDE SQUARE TO ROUND ADAPTER.
DESIGNER NOTES
1. THE AIR DEVICES SHOWN ARE TYPICAL. SCHEDULE SHALL BE ADJUSTED FOR PROJECT-SPECIFIC REQUIREMENTS.
2. SCHEDULE ADDITIONAL AIR DEVICES TO MEET PROJECT-SPECIFIC NEEDS.
3. FINAL DRAWING SIZE = 14 IN. WIDE

## SS233700-02
AIR DEVICE SCHEDULE (LINEAR) | [24 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | TYPE | AIR FLOW |  |  |  | MAX APD |  | MIN THROW |  | MAX THROW |  | # OF SLOTS | SLOT WIDTH |  | PANEL/FRAME SIZE |  | NECK SIZE |  | THROW PATTERN | THROW TYPE | NC | DAMPER | FINISH | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[15 empty] | IN | [mm] | IN | [mm]
|  | MIN |  | MAX
|  | CFM | [L/s] | CFM | [L/s] | IN WG | [Pa] | FT | [M] | FT | [M] |  | IN | [mm]
SD-31 | LINEAR | 180 | 85 | 580 | 270 | 0.268 | 66.7 | 4 - 7 -15 | 2.0 - 3.1 - 4.9 | 17 - 21 - 30 | 5.3 - 6.5 - 9.2 | 2 | 2 | 50 | 24 x 5 | [ 600 x 127 ] | 10 ø | [254 ø] | 2 WAY | VERTICAL | 41 | NONE | WHITE | -----
SD-32 | LINEAR | 150 | 71 | 510 | 240 | 0.279 | 69.4 | 4 - 8 - 16 | 2.2 - 3.3 - 5.0 | 18 - 22 - 31 | 5.4 - 6.6 - 9.3 | 2 | 2 | 50 | 24 x 5 | [ 600 x 127 ] | 12 ø | [305 ø] | 2 WAY | VERTICAL | 42 | NONE | WHITE | -----
SD-33 | LINEAR | 180 | 85 | 570 | 270 | 0.179 | 44.6 | 3 - 5 - 11 | 0.9 - 1.7 - 3.3 | 12 - 15 - 22 | 3.5 - 4.7 - 6.6 | 2 | 2.5 | 63 | 24 x 5 | [ 600 x 127 ] | 10 ø | [254 ø] | 2 WAY | VERTICAL | 43 | NONE | WHITE | -----
SD-34 | LINEAR | 210 | 99 | 660 | 310 | 0.24 | 59.8 | 4 - 6 - 13 | 1.2 - 1.9 - 3.9 | 13 - 17 - 23 | 4.1 - 5.0 - 7.1 | 2 | 2.5 | 63 | 24 x 5 | [ 600 x 127 ] | 12 ø | [305 ø] | 2 WAY | VERTICAL | 41 | NONE | WHITE | -----
SD-35 | LINEAR | 140 | 66 | 500 | 240 | 0.268 | 66.7 | 4 - 7 - 15 | 2.0 - 3.1 - 4.9 | 17 - 21 - 30 | 5.3 - 6.5 - 9.2 | 2 | 2 | 50 | 24 x 5 | [ 600 x 127 ] | 10 ø | [254 ø] | 2 WAY | HORIZONTAL | 41 | NONE | WHITE | -----
SD-36 | LINEAR | 150 | 71 | 510 | 240 | 0.279 | 69.4 | 4 - 8 - 16 | 2.2 - 3.3 - 5.0 | 18 - 22 - 31 | 5.4 - 6.6 - 9.3 | 2 | 2 | 50 | 24 x 5 | [ 600 x 127 ] | 12 ø | [305 ø] | 2 WAY | HORIZONTAL | 42 | NONE | WHITE | -----
SD-37 | LINEAR | 180 | 85 | 570 | 270 | 0.179 | 44.6 | 3 - 5 - 11 | 0.9 - 1.7 - 3.3 | 12 - 15 - 22 | 3.5 - 4.7 - 6.6 | 2 | 2.5 | 63 | 24 x 5 | [ 600 x 127 ] | 10 ø | [254 ø] | 2 WAY | HORIZONTAL | 43 | NONE | WHITE | -----
SD-38 | LINEAR | 210 | 99 | 660 | 310 | 0.24 | 59.8 | 4 - 6 -13 | 1.2 - 1.9 - 3.9 | 13 - 17 - 23 | 4.1 - 5.0 - 7.1 | 2 | 2.5 | 63 | 24 x 5 | [ 600 x 127 ] | 12 ø | [305 ø] | 2 WAY | HORIZONTAL | 41 | NONE | WHITE | -----
SD-39 | LINEAR | 20 | 9.4 | 200 | 94 | 0.335 | 83.3 | 2 - 3 - 6 | 0.5 - 0.9 - 1.8 | 17 - 21 - 30 | 5.2 - 6.4 - 9.0 | 1 | 1 | 25 | 48 x 3 | [ 1219 x 76 ] | 10 ø | [254 ø] | 1 WAY | VERTICAL | 42 | NONE | WHITE | -----
SD-310 | LINEAR | 50 | 24 | 350 | 170 | 0.256 | 63.8 | 4 - 5 - 11 | 1.1 - 1.6 - 3.3 | 23 - 28 - 39 | 6.9 - 8.4 - 11.9 | 2 | 1 | 25 | 48 x 5 | [ 1219 x 127 ] | 10 ø | [254 ø] | 1 WAY | VERTICAL | 32 | NONE | WHITE | -----
SD-311 | LINEAR | 30 | 14 | 240 | 110 | 0.363 | 90.3 | 2 - 4 - 7 | 0.7 - 1.1 - 2.3 | 19 - 23 - 33 | 5.7 - 7.0 - 9.9 | 1 | 1.5 | 38 | 48 x 4 | [ 1219 x 102 ] | 10 ø | [254 ø] | 1 WAY | VERTICAL | 36 | NONE | WHITE | -----
SD-312 | LINEAR | 40 | 19 | 400 | 190 | 0.252 | 62.7 | 1 - 3 -7 | 0.4 - 0.9 - 2.1 | 23 - 30 - 42 | 7.1 - 9.0 - 12.8 | 2 | 1.5 | 38 | 48 x 7 | [ 1219 x 178 ] | 10 ø | [254 ø] | 1 WAY | VERTICAL | 32 | NONE | WHITE | -----
SD-313 | LINEAR | 20 | 9.4 | 260 | 120 | 0.295 | 73.5 | 1 - 1 -4 | 0.2 - 0.4 - 1.3 | 19 - 24 - 34 | 5.6 - 7.3 - 10.3 | 1 | 2 | 50 | 48 x 5 | [ 1219 x 127 ] | 10 ø | [254 ø] | 1 WAY | VERTICAL | 37 | NONE | WHITE | -----
SD-314 | LINEAR | 40 | 19 | 460 | 220 | 0.286 | 71.2 | 1 - 1 - 5 | 0.2 - 0.4 - 1.6 | 26 - 36 - 51 | 8.0 - 10.9 - 15.4 | 2 | 2 | 50 | 48 x 9 | [ 1219 x 229 ] | 10 ø | [254 ø] | 1 WAY | VERTICAL | 33 | NONE | WHITE | -----
SD-315 | LINEAR | 20 | 9.4 | 320 | 150 | 0.374 | 96.1 | 0 - 1 - 3 | 0.1 - 0.2 - 0.9 | 22 - 29 - 41 | 6.7 - 8.8 - 12.4 | 1 | 2.5 | 63 | 48 x 6 | [ 1219 x 152 ] | 10 ø | [254 ø] | 1 WAY | VERTICAL | 40 | NONE | WHITE | -----
SD-316 | LINEAR | 40 | 19 | 580 | 270 | 0.286 | 71.2 | 1 - 1 - 5 | 0.2 - 0.4 - 1.6 | 26 - 36 - 51 | 8.0 - 10.9 - 15.4 | 2 | 2.5 | 63 | 48 x 11 | [ 1219 x 279 ] | 10 ø | [254 ø] | 1 WAY | VERTICAL | 37 | NONE | WHITE | -----
SD-317 | LINEAR | 20 | 9.4 | 380 | 180 | 0.374 | 93.1 | 0 - 1 - 3 | 0.1 - 0.2 - .09 | 22 - 29 - 41 | 6.7 - 8.8 - 12.4 | 1 | 3 | 75 | 48 x 7 | [ 1219 x 178 ] | 10 ø | [254 ø] | 1 WAY | VERTICAL | 35 | NONE | WHITE | -----
SD-318 | LINEAR | 50 | 24 | 650 | 310 | 0.247 | 68.1 | 1 - 2 - 6 | 0.2 - 0.5 - 1.9 | 27 - 38 - 54 | 8.1 - 11.5 - 16.3 | 2 | 3 | 75 | 48 x 13 | [ 1219 x 330 ] | 10 ø | [254 ø] | 1 WAY | VERTICAL | 33 | NONE | WHITE | -----
NOTES
1. SEE DETAIL FOR DAMPER IN BRANCH DUCT SERVING EACH DIFFUSER.
2. PROVIDE COLLAR AND TRANSITION AS REQUIRED.
DESIGNER NOTES
1. THE AIR DEVICES SHOWN ARE TYPICAL. SCHEDULE SHALL BE ADJUSTED FOR PROJECT-SPECIFIC REQUIREMENTS.
2. FINAL DRAWING SIZE = 20 IN. WIDE

## SS233700-03
AIR DEVICE SCHEDULE (RETURN) | [16 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | TYPE | AIR FLOW |  |  |  | MAX APD |  | MOUNTING | PANEL/FRAME SIZE |  | NECK SIZE |  | NC | DAMPER | FINISH | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  | MIN |  | MAX
|  | CFM | [L/s] | CFM | [L/s] | IN WG | [Pa] |  | IN x IN | [mm x mm] | IN x IN | [mm x mm]
RG-21 | PERFORATED | 60 | 28 | 100 | 47 | 0.088 | 22 | CEILING | 24 x 24 | [ 600 x 600 ] | 6 DIAM | [ 152 DIAM ] | 13 | NONE | WHITE | -----
RG-22 | PERFORATED | 110 | 52 | 170 | 80 | 0.088 | 22 | CEILING | 24 x 24 | [ 600 x 600 ] | 8 DIAM | [ 203 DIAM ] | 13 | NONE | WHITE | -----
RG-23 | PERFORATED | 170 | 80 | 250 | 120 | 0.088 | 22 | CEILING | 24 x 24 | [ 600 x 600 ] | 10 DIAM | [ 254 DIAM ] | 14 | NONE | WHITE | -----
RG-24 | PERFORATED | 240 | 110 | 400 | 190 | 0.088 | 22 | CEILING | 24 x 24 | [ 600 x 600 ] | 12 DIAM | [ 305 DIAM ] | 12 | NONE | WHITE | -----
RG-25 | PERFORATED | 320 | 150 | 500 | 240 | 0.087 | 22 | CEILING | 24 x 24 | [ 600 x 600 ] | 14 DIAM | [ 356 DIAM ] | 14 | NONE | WHITE | -----
RG-26 | PERFORATED | 420 | 200 | 700 | 330 | 0.087 | 22 | CEILING | 24 x 24 | [ 600 x 600 ] | 16 DIAM | [ 406 DIAM ] | 16 | NONE | WHITE | -----
RR-51 | RETURN REGISTER | 130 | 61 | 210 | 99 | 0.078 | 20 | WALL | 10 x 10 | [ 254 x 254 ] | 8 x 8 | [ 203 x 203 ] | 13 | OBD | WHITE | -----
RR-52 | RETURN REGISTER | 200 | 94 | 330 | 160 | 0.078 | 20 | WALL | 12 x 12 | [ 305 x 305 ] | 10 x 10 | [ 254 x 254 ] | 15 | OBD | WHITE | -----
RR-53 | RETURN REGISTER | 270 | 130 | 440 | 210 | 0.078 | 20 | WALL | 14 x 14 | [ 356 x 356 ] | 12 x 12 | [ 305 x 305 ] | 17 | OBD | WHITE | -----
RR-54 | RETURN REGISTER | 250 | 120 | 610 | 290 | 0.082 | 21 | WALL | 16 x 16 | [ 406 x 406 ] | 14 x 14 | [ 356 x 356 ] | 18 | OBD | WHITE | -----
RR-55 | RETURN REGISTER | 320 | 150 | 810 | 380 | 0.082 | 21 | WALL | 18 x 18 | [ 457 x 457 ] | 16 x 16 | [ 406 x 406 ] | 19 | OBD | WHITE | -----
RR-56 | RETURN REGISTER | 90 | 42 | 160 | 76 | 0.078 | 20 | WALL | 10 x 8 | [ 254 x 203 ] | 8 x 6 | [ 203 x 152] | 12 | OBD | WHITE | -----
RR-57 | RETURN REGISTER | 140 | 66 | 240 | 110 | 0.078 | 20 | WALL | 14 x 8 | [356 x 203 ] | 12 x 6 | [ 305 x 152 ] | 14 | OBD | WHITE | -----
RR-58 | RETURN REGISTER | 210 | 99 | 350 | 170 | 0.078 | 20 | WALL | 20 x 8 | [ 508 x 203 ] | 18 x 6 | [ 457 x 152 ] | 16 | OBD | WHITE | -----
RR-59 | RETURN REGISTER | 190 | 90 | 320 | 150 | 0.078 | 20 | WALL | 14 x 10 | [ 356 x 254 ] | 12 x 8 | [ 305 x 203 ] | 15 | OBD | WHITE | -----
RR-510 | RETURN REGISTER | 220 | 100 | 360 | 170 | 0.078 | 20 | WALL | 14 x 12 | [ 356 x 305 ] | 12 x 10 | [ 305 x 254 ] | 16 | OBD | WHITE | -----
RR-511 | RETURN REGISTER | 330 | 160 | 560 | 260 | 0.078 | 20 | WALL | 20 x 12 | [ 508 x 305 ] | 18 x 10 | [ 457 x 254 ] | 17 | OBD | WHITE | -----
RR-512 | RETURN REGISTER | 360 | 170 | 850 | 400 | 0.082 | 21 | WALL | 26 x 14 | [ 660 x 356 ] | 24 x 12 | [ 600 x 305 ] | 20 | OBD | WHITE | -----
RR-513 | RETURN REGISTER | 460 | 220 | 1260 | 590 | 0.095 | 24 | WALL | 32 x 14 | [ 813 x 356 ] | 30 x 12 | [ 762 x 305 ] | 24 | OBD | WHITE | -----
RG-61 | DRUM LOUVER | 100 | 47 | 200 | 94 | 0.091 | 23 | DUCT MOUNTED | 12 x 8 | [ 305 x 203 ] | 10 x 6 | [ 254 x 152 ] | 19 | NONE | WHITE | -----
RG-62 | DRUM LOUVER | 80 | 38 | 150 | 71 | 0.091 | 23 | DUCT MOUNTED | 14 x 6 | [ 356 x 152 ] | 12 x 4 | [ 305 x 102 ] | 15 | NONE | WHITE | -----
RG-63 | DRUM LOUVER | 150 | 71 | 290 | 140 | 0.091 | 23 | DUCT MOUNTED | 16 x 8 | [ 406 x 203 ] | 14 x 6 | [ 356 x 152 ] | 18 | NONE | WHITE | -----
RG-64 | DRUM LOUVER | 290 | 140 | 580 | 270 | 0.091 | 23 | DUCT MOUNTED | 22 x 10 | [ 560 x 254 ] | 20 x 8 | [ 508 x 203 ] | 21 | NONE | WHITE | -----
RG-65 | DRUM LOUVER | 450 | 210 | 900 | 420 | 0.091 | 23 | DUCT MOUNTED | 22 x 14 | [560 x 2356] | 20 x 12 | [ 508 x 305 ] | 23 | NONE | WHITE | -----
RG-66 | DRUM LOUVER | 670 | 320 | 1370 | 650 | 0.091 | 23 | DUCT MOUNTED | 32 x 14 | [ 813 x 356 ] | 30 x 12 | [ 762 x 305 ] | 25 | NONE | WHITE | -----
RG-67 | DRUM LOUVER | 550 | 260 | 1650 | 780 | 0.091 | 23 | DUCT MOUNTED | 38 x 14 | [ 965 x 356 ] | 36 x 12 | [ 914 x 305 ] | 25 | NONE | WHITE | -----
NOTE
PROVIDE SQUARE TO ROUND ADAPTER.
DESIGNER NOTES
1. THE AIR DEVICES SHOWN ARE TYPICAL. SCHEDULE SHALL BE ADJUSTED FOR PROJECT-SPECIFIC REQUIREMENTS.
2. DRAWING SIZE = 14 IN. WIDE

## SS233700-04
ROOM AIR BALANCE SCHEDULE
ROOM NO | ROOM NAME | AIR HANDLING UNIT NO | TERMINAL UNIT | INDIVIDUAL ROOM TEMP CONTROL | SUPPLY |  |  |  |  | RETURN OR EXHAUST | [5 empty] | ROOM AIR FLOW |  | ROOM AIR BALANCE | NET INFILTRATION |  | NET EXFILTRATION
[5 empty] | ROOM AIR FLOW |  | # OF AIR DEVICES | AIR DEVICE MARK | SUPPLY FAN | RETURN OR EXHAUST (R/E) | ROOM AIR FLOW |  | # OF AIR DEVICES | AIR DEVICE MARK | RETURN OR EXHAUST FAN | [7 empty] | REMARKS
[5 empty] | CFM | L/S |  |  |  |  | CFM | L/S |  |  |  | CV | VAV |  | CFM | [L/s] | CFM | [L/s]
1101 | MAIN LOBBY | 1-AHU4 | 1-TU-4-6 | Y | 4000 | 1900 | 4 | SD-66 | 1-SF4 | R | 3600 | 1700 | 4 | RG-66 | 1-RF4 |  | X | + |  | 0 | 400 | 190 | ----
1108 | PT ROOM | 1-AHU4 | 1-TU-4-7 | Y | 150 | 71 | 1 | SD-313 | 1-SF4 | R | 90 | 42 | 1 | RG-21 | 1-RF4 |  | X | 0 | 0 | 0 | 0 | 0 | 60 CFM TO TOILET EXHAUST
1110 | PT ROOM | 1-AHU4 | 1-TU-4-8 | Y | 150 | 71 | 1 | SD-313 | 1-SF4 | R | 90 | 42 | 1 | RG-21 | 1-RF4 |  | X | 0 | 0 | 0 | 0 | 0 | 60 CFM TO TOILET EXHAUST
1112 | ISO ROOM | 1-AHU4 | 1-TU-4-9 | Y | 300 | 140 | 1 | SD-314 | 1-SF4 | E | 350 | 170 | 1 | RG-24 | 1-EF4 | X |  | - | 50 | 24 |  | 0
1124 | TOILET | 1-AHU4 | N/A | N | N/A | N/A | N/A | N/A | 1-SF4 | E | 60 | 28 | 1 | RR-51 | 1-EF4 | X |  | - | 60 | 28 |  | 0
1130 | NURSES STATION | 1-AHU4 | 1-TU-4-10 | Y | 900 | 420 | 2 | SD-23 | 1-SF4 | R | 900 | 420 | 2 | RG-24 | 1-RF4 |  | X | 0 | 0 | 0 | 0 | 0
1132 | HAC | 1-AHU4 | N/A | N | N/A | N/A | N/A | N/A | 1-SF4 | E | 100 | 47 | 1 | RR-51 | 1-EF4 | X |  | - | 100 | 47 |  | 0
1134 | SOIL UTILITY | 1-AHU4 | N/A | N | N/A | N/A | N/A | N/A | 1-SF4 | E | 250 | 120 | 1 | RR-54 | 1-EF4 | X |  | - | 250 | 120 |  | 0
1135 | CLEAN UTLITY | 1-AHU4 | 1-TU-4-10 | Y | 200 | 94 | 1 | SD-22 | 1-SF4 | R | 180 | 85 | 1 | RR-51 | 1-RF4 | X |  | + |  | 0 | 20 | 9.4
1142 | EXAM ROOM | 1-AHU4 | 1-TU-4-14 | Y | 150 | 71 | 1 | SD-22 | 1-SF4 | R | 150 | 71 | 1 | RR-51 | 1-RF4 |  | X | 0 | 0 | 0 | 0 | 0
1148 | OFFICE | 1-AHU4 | 1-TU-4-16 | Y | 210 | 99 | 1 | SD-23 | 1-SF4 | R | 210 | 99 | 1 | RR-52 | 1-RF4 |  | X | 0 | 0 | 0 | 0 | 0
1150 | OFFICE | 1-AHU4 | 1-TU-4-18 | Y | 180 | 85 | 1 | SD-23 | 1-SF4 | R | 180 | 85 | 1 | RR-52 | 1-RF4 |  | X | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | [5 empty] | 0 | [7 empty] | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 | [7 empty] | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 | [7 empty] | 0 |  | 0
NOTE
ROOMS OR AREAS DO NOT HAVE INDIVIDUAL HUMIDITY CONTROL UNLESS NOTED.
DESIGNER NOTES
1. ALL ROOMS SHALL BE SCHEDULED.
2. ADD NOTES IN REMARKS FOR:
(a) INDIVIDUAL ROOM HUMIDITY CONTROL.
(b) CONNECTION TO SPECIAL EXHAUST.
(c) FILTERS REQUIRED FOR EXHAUST.
3. FINAL DRAWING SIZE = 19 IN. WIDE

## SS234000-01
AIR FILTER SCHEDULE | [16 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | MERV RATING | AIR FLOW |  | APD |  |  |  | HOUSING TYPE | CARTRIDGES |  |  |  |  | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[7 empty] | INITIAL |  | CHANGEOVER |  |  | # | SIZE |  | ARRANGEMENT | REMARKS
[5 empty] | CFM | [L/s] | IN | [mm] | IN | [mm] |  |  | IN | [mm]
1-PF1 | MER PENTHOUSE | 3 NORTH (BONE MARROW TRANSPLANT) | 1-AHU1 | 8 | 30000 | 14000 | 0.25 | 6.3 | 0.5 | 13 | SIDE | 18 | 24 x 24 x 2 | [ 600 x 600 x 50 ] | 6 WIDE BY 3 HIGH | -----
1-FF1 | MER PENTHOUSE | 3 NORTH (BONE MARROW TRANSPLANT) | 1-AHU1 | 14 | 30000 | 14000 | 0.65 | 16 | 1.3 | 33 | SIDE | 18 | 24 x 24 x 12 | [ 600 x 600 x 300 ] | 6 WIDE BY 3 HIGH | ----
1-FF1 | MER PENTHOUSE | 3 NORTH (BONE MARROW TRANSPLANT) | 1-AHU1 | 17 | 30000 | 14000 | 1 | 25 | 2 | 50 | SIDE | 18 | 24 x 24 x 12 | [ 600 x 600 x 300 ] | 6 WIDE BY 3 HIGH | ----
1-PF2 | MER PENTHOUSE | 4 NORTH (INTENSIVE CARE UNIT) | 1-AHU2 | 8 | 16000 | 7600 | 0.25 | 6.3 | 0.5 | 13 | SIDE | 10 | 24 x 24 x 2 | [ 600 x 600 x 50 ] | 5 WIDE BY 2 HIGH | -----
1-AF2 | MER PENTHOUSE | 4 NORTH (INTENSIVE CARE UNIT) | 1-AHU2 | 14 | 16000 | 7600 | 0.65 | 16 | 1.3 | 33 | SIDE | 10 | 24 x 24 x 12 | [ 600 x 600 x 300 ] | 5 WIDE BY 2 HIGH | ----
1-FF2 | MER PENTHOUSE | 4 NORTH (INTENSIVE CARE UNIT) | 1-AHU2 | 17 | 16000 | 7600 | 1 | 25 | 2 | 50 | SIDE | 10 | 24 x 24 x 12 | [ 600 x 600 x 300 ] | 5 WIDE BY 2 HIGH | ----
1-PF3 | MER PENTHOUSE | 3 EAST (MRI UNIT) | 1-AHU3 | 8 | 25000 | 12000 | 0.25 | 6.3 | 0.5 | 13 | SIDE | 15 | 24 x 24 x 2 | [ 600 x 600 x 50 ] | 5 WIDE BY 3 HIGH | -----
1-AF3 | MER PENTHOUSE | 3 EAST (MRI UNIT) | 1-AHU3 | 15 | 25000 | 12000 | 0.75 | 19 | 1.5 | 38 | SIDE | 15 | 24 x 24 x 16 | [ 600 x 600 x 400 ] | 5 WIDE BY 3 HIGH | ----
1-PF4 | MER PENTHOUSE | GYMNASIUM | 1-AHU4 | 8 | 28000 | 13000 | 0.25 | 6.3 | 0.5 | 13 | SIDE | 18 | 24 x 24 x 2 | [ 600 x 600 x 50 ] | 6 WIDE BY 3 HIGH | -----
1-AF4 | MER PENTHOUSE | GYMNASIUM | 1-AHU4 | 11 | 28000 | 13000 | 0.38 | 9.5 | 0.75 | 19 | SIDE | 18 | 24 x 24 x 4 | [ 600 x 600 x 100 ] | 6 WIDE BY 3 HIGH | ----
1-PF5 | MER PENTHOUSE | SURGICAL SUITE | 1-AHU5 | 11 | 39000 | 18000 | 0.38 | 9.5 | 0.75 | 19 | SIDE | 24 | 24 x 24 x 4 | [ 600 x 600 x 100 ] | 6 WIDE BY 4 HIGH | ----
1-AF5 | MER PENTHOUSE | SURGICAL SUITE | 1-AHU5 | 14 | 39000 | 18000 | 0.65 | 16 | 1.3 | 33 | SIDE | 24 | 24 x 24 x 12 | [ 600 x 600 x 300 ] | 6 WIDE BY 4 HIGH | ----
1-FF5 | MER PENTHOUSE | OR #1 | 1-AHU5 | 17 | 2000 | 940 | 0.9 | 23 | 1.6 | 40 | FRONT | 2 | 24 x 24 x 12 | [ 600 x 600 x 300 ] | 2 WIDE BY 1 HIGH | ----
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
[6 empty] | 0 |  | 0
DESIGNER NOTES
1. FOR ARRANGEMENT, INDICATE NUMBER WIDE x NUMBER HIGH. EXAMPLE: 3 WIDE x 2 HIGH.
2. SPECIFY HOUSING TYPE AS "SIDE SERVICE" OR "HOLDING FRAME." IT IS PERMISSIBLE TO SPECIFY FRONT OR BACK ACCESS IF SPACE DOES NOT ALLOW SIDE ACCESS.
3. SCHEDULE HEPA FILTERS AS BAG-IN/BAG-OUT TYPE. SEE SPECIFICATIONS SECTION 23 40 00, AIR FILTERS.
4. CALCULATE THE FAN STATIC PRESSURE BASED ON THE CHANGEOVER OR REPLACEMENT DROP VALUE.
5. VERIFY INITIAL, FINAL, AND CHANGEOVER STATIC PRESSURE DROPS.
6. UNLESS OTHERWISE INDICATED, ALL FILTERS SHALL BE 24" x 24" SIZE.
7. FINAL DRAWING SIZE = 16 IN. WIDE

## SS235011-01
BOILER PLANT · PUMP SCHEDULE | [22 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | CIRCULATING FLUID | [9 empty] | MIN % EFF | ELECTRICAL MOTOR | [6 empty] | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | FLUID | FLOW |  | HEAD |  | NPSH AVAILABLE |  | TEMPERATURE |  | SP GR |  | NOMINAL POWER |  | PHASE | VOLT | MAX RPM | SPEED CONTROL | REMARKS
[6 empty] | GPM | [L/s] | FT | [kPa] | FT | [kPa] | °F | [°C] |  |  | HP | [kW]
60-P1 | BOILER PLANT |  | FEEDWATER |  | FEEDWATER |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  |  | ----
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0 |  |  |  |  | ----
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0
[7 empty] | 0 |  | 0 |  | N/A | [5 empty] | 0
DESIGNER NOTE
FOR PARALLEL PUMPS, PUMPS ARE [100%/100%] [50%/50%] [ ] REDUNDANT.
FINAL DRAWING SIZE = 19 IN. WIDE
UPDATED: 12/1/2017

## SS235011-02
BOILER PLANT · FUEL OIL PUMP SCHEDULE | [18 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | TYPE | CAPACITY GPM [L/s] |  | DISCHARGE PRESS |  | OIL GRADE | OIL TEMP |  | VISCOSITY RANGE (SSU) | SUCTION LIFT |  | MOTOR |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  |  | GPM | [L/s] | PSIG | [kPa] |  | °F | [°C] |  | IN HG | [mm] | HP | [W] | PHASE | VOLT
FOP | BOILER PLANT |  |  |  | 0 |  | 0 | [7 empty] | 0
[5 empty] | 0 |  | 0 | [7 empty] | 0
[5 empty] | 0 |  | 0 | [7 empty] | 0
DESIGNER NOTE
FOR PARALLEL PUMPS, PUMPS ARE [100%/100%] [50%/50%] [ ] REDUNDANT.
FINAL DRAWING SIZE = 19 IN. WIDE
UPDATED: 12/1/2017

## SS235011-03
BOILER PLANT · FUEL OIL HEATER SCHEDULE | [19 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SERVICE AND/OR SYSTEM | OIL TYPE # | OIL TEMP |  |  |  | OIL FLOW |  | MAX OIL PRESS DROP |  | STEAM PRESS ENT CONTROL VALVE |  | STEAM CONTROL VALVE |  |  | STEAM TRAP CAPACITY LBS/HR [kg/s] |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  |  | ENT |  | LVG
|  |  |  | °F | [°C] | °F | [°C] | GPM | [L/s] | PSIG | [kPa] | PSIG | [kPa] | SIZE | LBS/HR | [kg/HR] | LBS/HR | [kg/HR]
60-FOHX1 | BOILER PLANT | [7 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0
[9 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0
[9 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 14 IN. WIDE
UPDATED: 12/1/2017

## SS235011-04
BOILER PLANT · FUEL OIL TANKS (BURNER FUEL) SCHEDULE | [9 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | FUEL OIL TYPE NO | NOM CAPACITY |  | DIMENSIONS | ALARM SYSTEM OR LEAK DETECTION | LEVEL INDICATOR | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  |  | GAL | [L]
60-FOT1 | YARD |  |  |  | 0
0
0
0
NOTES
1. THE CONSTRUCTION SHALL BE PER SPECIFICATIONS
2. INDICATE LOCATION: UNDERGROUND OR ABOVE GROUND.
DESIGNER NOTE
FINAL DRAWING SIZE 14 IN. WIDE
UPDATED: 12/1/2017

## SS235011-05
BOILER PLANT · CONDENSATE STORAGE TANK SCHEDULE | [9 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | MIN NET CAPACITY |  | DIMENSIONS (LENGTH) |  | DIMENSIONS (DIAMETER) |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  | GAL | [L] | IN | [mm] | IN | [mm]
60-CS1 | BOILER PLANT |  |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0
NOTE
TANK CONSTRUCTION SHALL BE PER SPECIFICAITONS: ASME CODE FOR 40 PSIG [276 kPa] MINIMUM WORKING PRESSURE.
DESIGNER NOTE
FINAL DRAWING SIZE = 12 IN. WIDE
UPDATED: 12/1/2017

## SS235011-06
BOILER PLANT · BLOWOFF TANK SCHEDULE | [9 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | MIN NET CAPACITY |  | DIMENSIONS (LENGTH) |  | DIMENSIONS (DIAMETER) |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  | GAL | [L] | IN | [mm] | IN | [mm]
60-BT1 |  |  |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0
NOTE
TANK CONSTRUCTION SHALL BE PER SPECIFICATIONS : ASME CODE FOR 40 PSIG [276 kPa] MINIMUM WORKING PRESSURE.
DESIGNER NOTE
FINAL DRAWING SIZE = 12 IN. WIDE
UPDATED: 12/1/2017

## SS235011-07
BOILER PLANT · ECONOMIZER SCHEDULE, FLUE GAS/FEEDWATER HEAT EXCHANGERS | [15 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | MIN HEAT EXCHANGED |  | WATER FLOW |  | MIN NET CAPACITY |  | MAX PRESS DROP WATER SIDE |  | MIN PRESS DROP GAS SIDE WC |  | DESIGN WATER TEMPERATURES DEG F |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  | MBH | [KW] | GPM | [L/s] | GAL | [L] | PSIG | [kPa] | IN | [mm] | IN | OUT
60-FHX1 | BOILER |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
NOTES
1. FEEDWATER INLET TEMPERATURE SHALL BE 228 °F [109 °C].
2. MINIMUM HEAT EXCHANGED AT 100% BOILER LOAD.
3. MINIMUM ALOWABLE FLUE GAS TEMPERATURE AFTER THE ECONOMIZER SHALL BE ____.
DESIGNER NOTE
FINAL DRAWING SIZE = 14 IN.WIDE
UPDATED: 12/1/2017

## SS235011-08
BOILER PLANT · AIR COMPRESSOR SCHEDULE | [16 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | STANDARD AIR INTAKE |  | ON/OFF CYCLE |  |  |  | RECEIVER SIZE |  | MOTOR |  |  |  |  | REMARKS
|  |  | SCFM | [L/s] | ON |  | OFF |  | GAL | [L] | POWER |  | VOLT | PHASE | RPM |  | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | PSI | [kPa] | PSI | [kPa] |  |  | HP | [W]
60-COMP-1 | BOILER PLANT |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
DESIGNER NOTES
1. FOR PLANTS WITH WATER TUBE BOILERS, THE SCFM SHALL BE 30 [10 CM/s] AND THE MOTOR SHALL BE 7.5 HP [5600 W].
2. FOR PLANTS WITH FIRE TUBE BOILERS, THE SCFM SHALL BE 11 [4 CM/s] AND THE MOTOR SHALL BE 3 HP [2238 W].
3. THE PRESSURE SHALL BE 100 PSIG [689 kPa].
4. THE RECEIVER SHALL HAVE A MINIMUM CAPACITY OF 80 GAL [303 L].
5. FINAL DRAWING SIZE = 16 IN. WIDE
UPDATED: 12/1/2017

## SS235011-09
BOILER PLANT · REFRIGERATED AIR DRYER SCHEDULE | [13 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | AIR QUANTITY |  | LEAVING AIR DEWPOINT |  | DESIGN OPERATING PRESSURE PSIG | MAXIMUM INLET AIR TEMPERATURE | MAXIMUM AMBIENT AIR TEMPERATURE |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[10 empty] | W | VOLT | PHASE
|  |  | SCFM | [L/s] | °F | [°C]
60-RAD-1 | BOILER PLANT |  |  | 0
0
0
DESIGNER NOTES
1. SCFM: TWO TIMES THE INSTRUMENT AND CONTROL AIR REQUIREMENT.
2. DEWPOINT 35-40 ˚F [1.5-4.4 ˚C] AT 100 PSIG [689 kPa].
3. FINAL DRAWING SIZE = 14 IN.WIDE
UPDATED: 12/1/2017

## SS235011-10
BOILER PLANT · STEAM VENT SILENCER SCHEDULE | [6 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | FLOW |  | OUTLET SIZE | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  | LBS/HR | [kg/HR]
60-SVS-1 | BOILER PLANT |  |  | 0
0
0
0
DESIGNER NOTES
1. THE STEAM VENT SILENCER SHALL USE SUPERHEATED STEAM APPROXIMATELY 300 ˚F [149 ˚C] AT 14.7 PSIG [101 kPa].
2. 12 DB MINIMUM AT 63 HZ; 17 DB MINIMUM AT 125-250 HZ; 25 DB MINIMUM AT 250-500 HZ; 34 DB MINIMUM AT 500-8000HZ.
3. FINAL DRAWING SIZE 10 IN. WIDE
UPDATED: 12/1/2017

## SS235011-11
BOILER PLANT · CONTINUOUS BLOWDOWN HEAT EXCHANGER SCHEDULE | [15 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | MAXIMUM OPERATING PRESSURE, PSIG | HEAT TRANSFER CAPACITY MBH | MAX INSIDE TUBES FLOW |  | TEMPERATURE |  |  |  | MAX PRESS DROP |  | OUTSIDE TUBES, WATER TEMP |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[7 empty] | IN |  | OUT
[5 empty] | GPM | [L/s] | °F | [°C] | °F | [°C] | PSIG | [kPa] | °F | [°C]
60-BHX1 | BOILER PLANT |  |  |  |  | 0 | [5 empty] | 0 |  |  | ---
[6 empty] | 0 | [5 empty] | 0
[6 empty] | 0 | [5 empty] | 0
NOTE
1. TUBE-TYPE HEAT EXCHANGERS IN CONDENSATE STORAGE TANK.
2. MANUFACTURER TO COORDINATE WITH CONDENSATE STORAGE TANK MANUFACTURER ON FLANGE CONNECTION SIZES, POSITION AT THE TANK, MINIMUM INTERIOR CLEARANCES, AND SUPPORTS AND BRACKETS INSIDE THE TANK, IF REQUIRED
3. OUTSIDE TUBE INLET TEMPERATURE BASED ON 80 ˚F [27 ˚C] EWT.
DESIGNER NOTE
FINAL DRAWING SIZE 14 IN. WIDE
UPDATED: 12/1/2017

## SS235011-12
BOILER PLANT · CHEMICAL FEED SYSTEMS, PUMP TYPE SCHEDULE | [10 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | FLOW RATE |  | DISCHARGE PRESSURE |  | PUMP POWER |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  | GPM | [L/s] | PSIG | [kPa] | [W] | PHASE | VOLTS
60-CFP1 | BOILER PLANT |  |  | 0 |  | 0
|  |  |  | 0 |  | 0
|  |  |  | 0 |  | 0
|  |  |  | 0 |  | 0
DESIGNER NOTES
1. PACKAGED-TYPE TANK PUMP [AND AGITATOR] ASSEMBLY.
2. METERING PUMP CAPACITY SHALL BE 0-2 GPM [0-7.6 L/HR] ADJUSTABLE.
3. PUMP DISCHARGE PRESSURE SHALL BE MINIMUM 110-150 PSIG [758-1034 kPa] AND AS REQUIRED TO OVERCOME THE PRESSURE DROPS INDICATED IN THE SPECIFICAIIONS.
4. THE PUMP MOTOR SHALL BE MINIMUM .33 HP [248 W], 120 VOLTS, AND 1 PHASE .
5. IF REQUIRED, THE AGITATOR MOTOR SHALL BE .33 HP [248 W], 120 VOLTS, AND 1 PHASE.
6. THE TANK SHALL HAVE A CAPACITY OF 50 GAL [180 L].
7. FINAL DRAWING SIZE = 12 IN. WIDE
8. REFER TO SPECIFCATION SECTION 23 50 11 FOR ADDITIONAL INFORMATION.
UPDATED: 12/1/2017

## SS235011-13
BOILER PLANT · EMERGENCY GAS SAFETY SHUT-OFF VALVES SCHEDULE | [23 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | EV-1 MAIN GAS | [9 empty] | EV-2 IGNITER GAS | [9 empty] | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  | FLOW RATE |  | INLET PRESS |  | MAX PRESS DROP |  | MIN DESIGN PRESS |  | VALVE BODY PIPE SIZE |  | FLOW RATE |  | INLET PRESS |  | MAX PRESS DROP |  | MIN DESIGN PRESS |  | VALVE BODY PIPE SIZE
|  |  | CFH | [L/m] | PSIG | [kPa] | PSIG | [kPa] | PSIG | [kPa] | IN | [mm] | CFH | L/m | PSIG | [kPa] | PSIG | [kPa] | PSIG | [kPa] | IN | [mm]
60-EGS1 | BOILER PLANT |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
NOTES
1. THE MAIN GAS VALVE SHALL HAVE THE SPECIFIC GRAVITY OF NATURAL GAS WITH A FLOW, CFH [CM/s] OF 0.6 TIMES THE MAXIMUM FLOW.
2. THE IGNITER GAS VALVE SHALL HAVE THE SPECIFIC GRAVITY OF PROPANE WITH A FLOW, CFH [CM/s] OF 0.6 TIMES THE MAXIMUM FLOW.
DESIGNER NOTE
FINAL DRAWING SIZE 19 IN. WIDE
UPDATED: 12/1/2017

## SS235225-01
LOW PRESSURE HOT WATER BOILER, PACKAGED TYPE, FACTORY ASSEMBLED | [30 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | TYPE | MAX OUTPUT CAPACITY |  | OPERATING PRESS |  | RELIEF VALVE SETTING |  | EWT |  | LWT |  | WATER FLOW RATE |  | WATER PRESSURE DROP AT RATED FLOW |  | NATURAL GAS |  |  |  | # 2 OIL |  |  |  | FORCED DRAFT FAN MOTOR |  |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[17 empty] | INPUT |  | OUTPUT |  | INPUT |  | OUTPUT |  | POWER |  | PHASE | VOLT | RPM
|  |  | BTU/HR | [kW] | PSIG | [kPa] | PSIG | [kPa] | DEG F | [DEG C] | DEG F | [DEG C] | GPM | [LPM] | FT | [kPA] | MBH | [kW] | MBH | [kW] | MBH | [kW] | MBH | [kW] | HP | [W]
60-BWT1 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | -----
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0
NOTES
1. MINIMUM EFFICIENCY AT FULL LOAD FOR NON-CONDENSING BOILERS IS ________ PERCENT AND FOR CONDENSING BOILERS IS ________ PERCENT.
2. DESIGN PRESSURE IS 150 PSIG [1034 kPa] MINIMUM.
3. ALTITUDE IS _____FT [ M] ABOVE SEA LEVEL.
DESIGNER NOTES
1. FINAL DRAWING SIZE = 26 IN. WIDE
2. FOR TYPE, ENTER "CONDENSING" OR "NON-CONDENSING" AND IDENTIFY HEAT EXCHANGER TYPE.
3. IF WATER FLOW RATE THROUGH THE BOILER IS INTENDED TO VARY WITH LOAD CONDITIONS, PROVIDE A MEANS TO VERIFY THAT THE MANUFACTURER'S MINIMUM FLOW RATE IS MAINTAINED.
UPDATED: 12/1/2017
ENTIRE SCHEDULE IS NEW

## SS235233-01
BOILER PLANT · WATER TUBE STEAM BOILER SCHEDULE, PACKAGED TYPE, SHOP ASSEMBLED | [40 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | TYPE | MAX CAPACITY |  | BOILER |  | OPERATING PRESS |  | RELIEF VALVE SETTING |  | HEATING SURFACE |  | SURFACE VOL |  | MIN CONT FIRING RATE |  | NATURAL GAS |  |  |  | # 2 OIL |  |  |  | FIRST CUTOUT SETTINGS |  | SECOND CUTOUT SETTINGS |  | OIL ATOM COMPRESS MOTOR |  |  |  |  | FORCED DRAFT FAN MOTOR |  |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[18 empty] | INPUT |  | OUTPUT |  | INPUT |  | OUTPUT | [5 empty] | POWER |  | PHASE | VOLT | RPM | POWER |  | PHASE | VOLT | RPM
|  |  |  | LBS/HR | [kg/HR] | HP | [kW] | PSIG | [kPa] | PSIG | [kPa] | SQ FT | [SQ M] | CFT | [CM] | LBS/HR | [kg/HR] | MBH | [kW] | MBH | [kW] | MBH | [kW] | MBH | [kW] | PSIG | [kPa] | PSIG | [kPa] | HP | [W] |  |  |  | HP | [W]
60-BWT1 | BOILER PLANT |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0 |  |  |  | -----
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0
0
NOTES
1. STEAM QUALITY IS 99% MINIMUM.
2. DESIGN PRESSURE IS 200 PSIG [1378 kPa] MINIMUM.
3. FEEDWATER TEMPERATURE IS 212 ˚F [100 ˚C] MINIMUM, AND 228 ˚F [109 ˚C] NORMAL.
4. FOR STEAM NOZZLE FORCES AND MOMENTS, SEE DRAWING # _________.
5. ALTITUDE IS _____FT [ M] ABOVE SEA LEVEL.
6. THERE SHALL BE 5 PSIG [35 kPa] BETWEEN VALVES.
DESIGNER NOTES
1. FINAL DRAWING SIZE = 26 IN. WIDE
2. ENTER BOILER TYPE AS "D-TYPE" OR "FLEXIBLE WATER TUBE.
UPDATED: 12/1/2017

## SS235239-01
BOILER PLANT · FIRE TUBE STEAM BOILER SCHEDULE, PACKAGED TYPE, SHOP ASSEMBLED | [40 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | TYPE | MAX CAPACITY |  | BOILER |  | OPERATING PRESS |  | RELIEF VALVE SETTING |  | HEATING SURFACE |  | MIN CONT FIRING RATE |  | NATURAL GAS |  |  |  | # 2 OIL |  |  |  | RELIEF VALVE SETTING |  | FIRST CUTOUT SETTINGS |  | SECOND CUTOUT SETTINGS |  | OIL ATOM COMPRESS MOTOR |  |  |  |  | FAN MOTOR |  |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[16 empty] | INPUT |  | OUTPUT |  | INPUT |  | OUTPUT | [7 empty] | POWER |  | PHASE | VOLT | RPM | POWER |  | PHASE | VOLT | RPM
|  |  |  | LBS/HR | [kg/HR] | HP | [kW] | PSIG | [kPa] | PSIG | [kPa] | SQ FT | [SQ M] | LBS/HR | [kg/HR] | MBH | [kW] | MBH | [kW] | MBH | [kW] | MBH | [kW] | PSIG | [kPa] | PSIG | [kPa] | PSIG | [kPa] | HP | [W] |  |  |  | HP | [W]
60-BFT1 | BOILER PLANT |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0 |  |  |  | -----
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  |  |  | 0
NOTES
1. STEAM QUALITY IS 99% MINIMUM.
2. DESIGN PRESSURE IS 200 PSIG [1378 kPa] MINIMUM.
3. FEEDWATER TEMPERATURE IS 212 ˚F [100 ˚C] MINIMUM, AND 228 ˚F [109 ˚C] NORMAL.
4. FOR STEAM NOZZLE FORCES AND MOMENTS, SEE DRAWING # _________.
5. ALTITUDE IS _____FT [ M] ABOVE SEA LEVEL.
6. THERE SHALL BE 5 PSIG [35 kPa] BETWEEN VALVES.
DESIGNER NOTE
FINAL DRAWING SIZE = 26 IN. WIDE
UPDATED: 12/1/2017

## SS235239-02
HOT WATER HEATING BOILER SCHEDULE | [29 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | FLUID | [7 empty] | BOILER | [5 empty] | % EFF | NATURAL GAS SUPPLY PRESSURE |  | FUEL | RELIEF VALVE SETTING |  | ELECTRICAL |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | FLOW |  | EWT |  | LWT |  | WPD |  | POWER |  | OUTPUT GENERATED |  | MAX HEAT INPUT | [7 empty] | POWER |  | PHASE | VOLT
[5 empty] | GPM | [LPS] | °F | [°C] | °F | [°C] | FT | [kPa] | HP | [kW] | MBH | [kW] | MBH | [kW] |  | IN WG | [Pa] |  | PSIG | [kPa] | HP | [W]
7-BHW1 | B1100 | NURSING HOME | BUILDING HOT WATER | CONDENSING | 240 | 15 | 90 | 32.2 | 120 | 48.9 | 18 | 54 |  |  | 2640 | 770 | 3100 | 910 | 85 | 14 | 3500 | NG | 75 | 520 | 1 | 750 | 1 | 120 | -----
22-BHW1 | B1200 | OFFICES | BUILDING HOT WATER | CAST IRON | 160 | 10 | 120 | 48.9 | 160 | 71.1 | 13 | 39 |  |  | 3280 | 960 | 4000 | 1200 | 82 | 14 | 3500 | NG | 75 | 520 | 1 | 750 | 1 | 120
46-BHW1 | B1300 | MANFG | PROCESSES | FIRE TUBE | 560 | 35 | 120 | 48.9 | 180 | 82.2 | 20 | 60 |  |  | 16738 | 4900 | 21000 | 6200 | 80 | 14 | 3500 | NG | 75 | 520 | 7.5 | 5600 | 3 | 400
[6 empty] | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 20 IN. WIDE
UPDATED: 12/1/2017

## SS236400-01
WATER COOLED CHILLER SCHEDULE | [31 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | TYPE | CAPACITY |  | MAX kW/TON | MIN COP | MAX IPLV (kW/TON) | EVAPORATOR | [8 empty] | CONDENSER | [8 empty] | ELECTRICAL |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[9 empty] | FLOW |  | EWT |  | LWT |  | MAX WPD |  | FOULING FACTOR | FLOW |  | EWT |  | LWT |  | MAX WPD |  | FOULING FACTOR | POWER | PHASE | VOLT | SPEED CONTROL
|  |  |  | TONS | [kW] |  |  |  | GPM | [L/s] | °F | [°C] | °F | [°C] | FT | [kPa] |  | GPM | [L/s] | °F | [°C] | °F | [°C] | FT | [kPa] |  | MCA
18-WCCH1 | BLDG 18 | OUTPATIENT | HELICAL ROTARY | 100 | 28 | 0.7 | 5 | 0.51 | 230 | 15 | 56 | 13.3 | 42 | 5.6 | 12 | 36 | 0.0001 | 300 | 19 | 85 | 29.4 | 95 | 35 | 14 | 42 | 0.00025 | 130 | 3 | 460 | CONSTANT | SINGLE POINT POWER CONNECTION
18-WCCH2 | BLDG 18 | BUILDING 1 | CENTRIFUGAL 2 STAGE | 1000 | 280 | 0.55 | 6.4 | 0.45 | 2200 | 140 | 56 | 13.3 | 42 | 5.6 | 10 | 30 | 0.0001 | 3000 | 190 | 85 | 29.4 | 95 | 35 | 12 | 36 | 0.00025 | 970 | 3 | 460 | CONSTANT | SINGLE POINT POWER CONNECTION
[5 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
[5 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
[5 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
[5 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
[5 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0 |  |  | 0 | [5 empty] | 0
NOTES
1. SEE SPECIFICATIONS FOR OTHER APPLICABLE ENGINEERING REQUIREMENTS.
2. "MAX kW/TON" AND "MIN COP" SPECIFIED ARE AT DESIGN CONDITION INDICATED.
3. BOTH THE EVAPORATOR AND CONDENSER SHALL BE DESIGNED FOR VARIABLE FLOW.
DESIGNER NOTES
1. USE IPLV WHEN SELECTING THE CHILLER AT THE STANDARD ARI CONDITIONS. USE NPLV WHEN SELECTING THE CHILLER AT OPERATING PARAMETERS OTHER THAN STANDARD ARI CONDITIONS.
2. FINAL DRAWING SIZE = 23 IN. WIDE

## SS236400-02
AIR COOLED CHILLER SCHEDULE | [31 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | TYPE | CAPACITY |  | # OF COMP | MAX kW/TON | MIN COP | MAX IPLV (kW/TON) | EVAPORATOR | [8 empty] | CONDENSER |  | ELECTRICAL | [9 empty] | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[10 empty] | FLOW |  | EWT |  | LWT |  | MAX WPD |  | FOULING FACTOR | AMBIENT OA TEMP |  | COMPRESSOR MOTOR |  |  |  |  | CONDENSER FAN MOTORS
[21 empty] | # COMP | HP | [kW] | PHASE | VOLT | # FANS | NOMINAL POWER |  | PHASE | VOLT
|  |  |  | TONS | [kW] |  |  |  |  | GPM | [L/s] | °F | [°C] | °F | [°C] | FT | [kPa] |  | °F | [°C] | [6 empty] | HP | [W]
18-ACCH1 | BLDG 18 | CLINIC | SCREW | 165 | 580 | 2 | 1.2 | 3 | 0.85 | 280 | 18 | 56 | 13.3 | 42 | 5.6 | 12 | 36 | 0.0001 | 95 | 35 | 2 | 85 | 63 | 3 | 460 | 12 | 2 | 1500 | 3 | 460
[5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0
[5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0
[5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0
[5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0
[5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0
[5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0
NOTES
1. SEE SPECIFICATIONS FOR OTHER APPLICABLE ENGINEERING REQUIREMENTS.
2. "MAX kW/TON" AND "MIN COP" SPECIFIED ARE AT DESIGN CONDITIONS INDICATED. kW/TON INCLUDES CONDENSER FANS.
DESIGNER NOTES
1. USE IPLV WHEN SELECTING THE CHILLER AT THE STANDARD ARI CONDITIONS. USE NPLV WHEN SELECTING THE CHILLER AT OPERATING PARAMETERS OTHER THAN STANDARD ARI CONDITIONS.
2. FINAL DRAWING SIZE = 23 IN. WIDE

## SS236400-03
REMOTE CONDENSER CHILLER SCHEDULE | [30 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | TYPE | CAPACITY |  | MAX kW/TON | MIN COP | MAX IPLV (kW/TON) | EVAPORATOR | [8 empty] | AMBIENT OA TEMP |  | ELECTRICAL | [9 empty] | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[9 empty] | FLOW |  | EWT |  | LWT |  | MAX WPD |  | FOULING FACTOR |  |  | COMPRESSOR MOTOR |  |  |  |  | CONDENSER FAN MOTORS
[20 empty] | # COMP | NOMINAL POWER |  | PHASE | VOLT | # FANS | NOMINAL POWER |  | PHASE | VOLT
|  |  |  | TONS | [kW] |  |  |  | GPM | [L/s] | °F | [°C] | °F | [°C] | FT | [kPa] |  | °F | [°C] |  | HP | [kW] |  |  |  | HP | [W]
20-RCCH1 | BLDG 20 | OUTPATIENT | SCREW | 75 | 21 | 1.25 | 2.8 | 1.1 | 130 | 8.2 | 56 | 13.3 | 42 | 5.6 | 8 | 24 | 0.0001 | 95 | 35 | 2 | 40 | 30 | 3 | 460 | 4 | 1 | 750 | 3 | 460 | ----
[5 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0
[5 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0
[5 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0
[5 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0
[5 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0
[5 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0
[5 empty] | 0 |  |  |  |  | 0 | [5 empty] | 0 | [5 empty] | 0 |  |  |  |  | 0
NOTES
1. SEE SPECIFICATIONS FOR OTHER APPLICABLE ENGINEERING REQUIREMENTS.
2. "MAX kW/TON" AND "MIN COP" SPECIFIED ARE NOT DESIGN CONDITIONS INDICATED.
DESIGNER NOTES
1. USE IPLV WHILE SELECTING THE CHILLER AT THE STANDARD ARI CONDITIONS. USE NPLV WHILE SELECTING THE CHILLER AT OPERATING PARAMETERS OTHER THAN STANDARD ARI CONDITIONS.
2. FINAL DRAWING SIZE = 23 IN. WIDE

## SS236400-04
AIR COOLED CONDENSING UNIT SCHEDULE (AIR CONDITIONING SERVICE) | [24 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | MIN REFRIGERATION |  | REFRIGERANT | MAX SUCTION TEMP @ COMP |  | OA TEMP |  | MIN EER | IPLV | COMPRESSOR MOTOR |  |  |  |  | CONDENSER FAN MOTOR |  |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[14 empty] | # COMP | NOMINAL POWER |  | PHASE | VOLT | # FANS | NOMINAL POWER |  | PHASE | VOLT
[5 empty] | MBH | [kW] |  | °F | [°C] | °F | [°C] |  |  |  | HP | [kW] |  |  |  | HP | [W]
20-ACCU1 | GRADE | CLINCAL | 1-FCU5 | SCROLL | 370 | 1300 | 410a | 42 | 5.6 | 110 | 43.3 | 11.1 | 16.2 | 1 | 35 | 26 | 3 | 460 | 3 | 1 | 750 | 1 | 120 | -----
[6 empty] | 0 | [9 empty] | 0 |  |  |  |  | 0
[6 empty] | 0 | [9 empty] | 0 |  |  |  |  | 0
[6 empty] | 0 | [9 empty] | 0 |  |  |  |  | 0
[6 empty] | 0 | [9 empty] | 0 |  |  |  |  | 0
[6 empty] | 0 | [9 empty] | 0 |  |  |  |  | 0
[6 empty] | 0 | [9 empty] | 0 |  |  |  |  | 0
[6 empty] | 0 | [9 empty] | 0 |  |  |  |  | 0
[6 empty] | 0 | [9 empty] | 0 |  |  |  |  | 0
[6 empty] | 0 | [9 empty] | 0 |  |  |  |  | 0
[6 empty] | 0 | [9 empty] | 0 |  |  |  |  | 0
[6 empty] | 0 | [9 empty] | 0 |  |  |  |  | 0
NOTES
1. UL-RATED STARTERS SHALL BE FURNISHED BY MANUFACTURER OF EQUIPMENT.
2. kW/TON INCLUDES CONDENSER FANS.
DESIGNER NOTES
FINAL DRAWING SIZE = 19 IN. WIDE

## SS236500-01
COOLING TOWER SCHEDULE | [31 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SERVICE | TOWER TYPE | TOTAL NOMINAL CAPACITY |  | # CELLS | FLOW RATE EACH CELL |  | WPD |  | TEMPERATURE | [5 empty] | FAN MOTOR | [6 empty] | SUMP HEATER |  |  | MAX OPERATING WEIGHT |  | MAX HEIGHT W/HANDRAIL |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[11 empty] | AMBIENT Wb |  | EWT |  | LWT |  | NO | POWER |  | PHASE | VOLT | RPM | SPEED CONTROL | TYPE | CAPACITY
|  |  |  | TONS | [kW] |  | GPM | [L/s] | FT | [kPa] | °F | [°C] | °F | [°C] | °F | [°C] |  | HP | [kW] | [5 empty] | BTUH | [W] | LB | [kg] | FT | [M]
1-CT1 | ROOF | CONDENSER WATER | CROSS FLOW | 400 | 110 | 2 | 600 | 38 | 10 | 30 | 76 | 24.4 | 96 | 35.6 | 85 | 29.4 | 2 | 15 | 11 | 3 | 460 | 1750 | VARIABLE | ELECTRIC IMMERSION | 40000 | 12000 | 11500 | 5200 | 20 | 6
[5 empty] | 0 |  |  | 0 |  | 0 | [8 empty] | 0 | [6 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  |  | 0 |  | 0 | [8 empty] | 0 | [6 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  |  | 0 |  | 0 | [8 empty] | 0 | [6 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  |  | 0 |  | 0 | [8 empty] | 0 | [6 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  |  | 0 |  | 0 | [8 empty] | 0 | [6 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  |  | 0 |  | 0 | [8 empty] | 0 | [6 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  |  | 0 |  | 0 | [8 empty] | 0 | [6 empty] | 0 |  | 0 |  | 0
[5 empty] | 0 |  |  | 0 |  | 0 | [8 empty] | 0 | [6 empty] | 0 |  | 0 |  | 0
DESIGNER NOTES
1. RAISE COOLING TOWER TO ENSURE THE REQUIRED NET POSITIVE HEAD OF THE CONDENSER WATER PUMP IS MET.
2. FOR ROOF INSTALLATIONS, RAISE COOLING TOWER A MINIMUM OF FOUR FT [12 M] ABOVE ROOF.
3. COORDINATE SCREEN HEIGHT WITH TOTAL DEVELOPED HEIGHT INCLUDING RE-ROOF CLEARANCE, STRUCTURAL STEEL, VIBRATION ISOLATION, HAND RAILS, PIPING, AND FAN SHROUD.
4. PROVIDE NIGHT SERVICE LIGHTING.
5. PROVIDE MAKE-UP WATER METER AND BLOWDOWN ELAPSED TIMER (NON-RESETTABLE) FOR EACH TOWER.
6. SHOW WINTER CONDITIONS IN HYDRONIC ECONOMIZER CYCLE USED.
7. FINAL DRAWING SIZE = 23 IN. WIDE

## SS237200-01
HEAT PIPE AIR TO AIR HEAT EXCHANGER SCHEDULE | [32 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | MODE | MIN SUPPLY AIR EFF % | SUPPLY AIR | [11 empty] | EXHAUST AIR | [14 empty] | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | SUPPLY AIR FLOW |  | APD |  | EAT |  |  |  | LAT |  |  |  | EXHAUST AIR FLOW |  | APD |  | EAT |  |  |  | LAT |  |  |  | ELECTRICAL DATA
[9 empty] | Db |  | Wb |  | Db |  | Wb | [5 empty] | Db |  | Wb |  | Db |  | Wb
[5 empty] | CFM | [L/s] | IN | [Pa] | °F | [°C] | °F | [°C] | °F | [°C] | °F | [°C] | CFM | [L/s] | IN | [mm] | °F | [°C] | °F | [°C] | °F | [°C] | °F | [°C] | [W] | PHASE | VOLT
10-AAHX1 | B1100 | 10-AHU1 | COOLING | 58% | 8000 | 3800 | 0.9 | 230 | 95 | 35 | 78 | 25.6 | 78 | 25.6 | 74 | 23.3 | 8000 | 3800 | 0.9 | 23 | 75 | 23.9 | 62 | 16.7 | 90 | 32.2 | 67 | 19.4 | 300 | 1 | 120
|  |  | HEATING | 58% | 8000 | 3800 | 0.9 | 230 | 35 | 1.7 | 30 | -1.1 | 60 | 15.6 | 44 | 6.7 | 8000 | 3800 | 0.9 | 23 | 72 | 22.2 | 55 | 12.8 | 46 | 7.8 | 44 | 6.7
[6 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0
[6 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0
[6 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0
[6 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0
[6 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0
[6 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0
[6 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0
[6 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0
[6 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0
[6 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0
DESIGNER NOTES
1. PROVIDE A VA GRADE A PREFILTER ON EXHAUST.
2. FINAL DRAWING SIZE = 23 IN. WIDE

## SS237200-02
ROTARY AIR TO AIR HEAT RECOVERY WHEEL SCHEDULE | [32 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | MODE | SUPPLY AIR | [11 empty] | EXHAUST AIR | [11 empty] | ROTOR MOTOR |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  |  | SUPPLY AIR FLOW |  | APD |  | EAT |  |  |  | LAT |  |  |  | AIR FLOW |  | APD |  | EAT |  |  |  | LAT
[8 empty] | Db |  | Wb |  | Db |  | Wb | [5 empty] | Db |  | Wb |  | Db |  | Wb |  | HP | [kW] | PHASE | VOLT
|  |  |  | CFM | [L/s] | IN | [Pa] | °F | [°C] | °F | [°C] | °F | [°C] | °F | [°C] | CFM | [L/s] | IN | [mm] | °F | [°C] | °F | [°C] | °F | [°C] | °F | [°C]
2-RAHX1 | B1200 | 2-AHU1 | SUMMER | 12000 | 5700 | 0.7 | 75 | 90 | 32.2 | 77 | 25 | 75 | 23.9 | 73 | 22.8 | 10800 | 5100 | 0.7 | 18 | 75 | 23.9 | 61 | 16.1 | 90 | 32.2 | 65 | 18.3 | 0.75 | 0.6 | 3 | 208
|  |  | WINTER | 12000 | 5700 | 0.7 | 18 | 2 | -16.7 | 10 | -12.2 | 58 | 14.4 | 38 | 3.3 | 10800 | 5100 | 0.7 | 18 | 70 | 21.1 | 54 | 12.2 | 45 | 7.2 | 42 | 5.6
[5 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0 | [9 empty] | 0
[5 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0 | [9 empty] | 0
[5 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0 | [9 empty] | 0
[5 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0 | [9 empty] | 0
[5 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0 | [9 empty] | 0
[5 empty] | 0 |  | 0 | [9 empty] | 0 |  | 0
DESIGNER NOTES
1. PROVIDE A VA GRADE A PREFILTER ON EXHAUST.
2. FINAL DRAWING SIZE = 23 IN. WIDE

## SS237300-01
MAKE-UP AIR HEATING AND VENTILATING UNIT SCHEDULE | [17 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | TYPE | MAX CAPACITY |  | MIN AIR FLOW |  | SUPPLY FAN MARK | EXHAUST FAN MARK | PREFILTER MARK | AFTER FILTER MARK | PREHEAT COIL MARK | TEMPERATURES |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[13 empty] | EAT |  | LAT
|  |  |  | MBH | [kW] | CFM | [L/s] | [5 empty] | °F | [°C] | °F | [°C]
20-MAU1 | RM 1108 | KITCHEN | PREHEAT | 206 | 700 | 3600 | 1700 | 1-SF5 | 1-EF5 | 1-PF5 | 1-AF5 | 1-PHC5 | 24 | -4.4 | 77 | 25 | -----
[5 empty] | 0 |  | 0
[5 empty] | 0 |  | 0
[5 empty] | 0 |  | 0
[5 empty] | 0 |  | 0
[5 empty] | 0 |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 14 IN. WIDE

## SS237300-02
AIR HANDLING UNIT SCHEDULE | [22 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | TYPE | AIR FLOW | AIR FLOW | [5 empty] | SUPPLY FAN MARK | RETURN OR RELIEF FAN MARK | EXHAUST FAN MARK | PREFILTER MARK | AFTER FILTER MARK | FINAL FILTER MARK | HEAT RECOVERY MARK | PREHEAT COIL MARK | COOLING COIL MARK | REHEAT COIL | HUMIDIFIER MARK | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | SUPPLY |  | MIN OA |  | RETURN
[5 empty] | CFM | [L/s] | CFM | [L/s] | CFM | [L/s]
1-AHU5 | E9100A | 3 NORTH | PRE-ENGINEERING | VAV | 26000 | 12000 | 5000 | 2400 | 21000 | 9900 | 1-SF5 | 1-RF5 | 1-EF5 | 1-PF5 | 1-AF5 | 1-FF5 | N/A | 1-PHC5 | 1-CC5 | AT TU | 1-H5 | -----
[6 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0
[6 empty] | 0 |  | 0 |  | 0
DESIGNER NOTES
1. FOR AREA SERVED, WHERE APPLICABLE, SHOW FUNCTIONAL AREA, SUCH AS SURGERY, KITCHEN, LABORATORIES, ETC. OTHERWISE, SHOW FLOORS SERVED FOR TYPE OF SYSTEM.
2. MINIMUM OA IS A CALCULATED VALUE, BUT NOT LESS THAN 15%.
3. FINAL DRAWING SIZE = 20 IN. WIDE

## SS237300-03
PACKAGED EVAPORATIVE COOLER SCHEDULE | [32 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | TYPE | AIR FLOW |  | MAX FACE VELOCITY |  | MIN AVAILABLE EXT SP |  | TEMPERATURES | [7 empty] | % SATURATION EFFICIENCY | SUPPLY FAN |  |  |  | SPEED CONTROL | CIRCULATING PUMP |  |  |  | MIN BLEEDOFF |  | OVERALL DIMENSIONS (HEIGHT BY WIDTH) |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[10 empty] | EAT Db |  | EAT Wb |  | LAT Db |  | LAT Wb |  |  | FAN POWER |  | PHASE | VOLT |  | NOMINAL POWER |  | PHASE | VOLT
|  |  |  | CFM | [L/s] | FPM | [M/s] | WG | [Pa] | °F | [°C] | °F | [°C] | °F | [°C] | °F | [°C] |  | HP | [W] |  |  |  | HP | [W] |  |  | GPH | [L/H] | IN | [mm]
30-EC6 | ROOF | CENTRAL PLANT | HORIZONTAL DISCHARGE | 10000 | 4700 | 400 | 2 | 0.7 | 180 | 105 | 40.6 | 70 | 21.1 | 74 | 23.3 | 70 | 21.1 | 90% | 3 | 2200 | 3 | 460 | VFD | 0.5 | 370 | 1 | 120 | 18 | 68 | 50 X 64 | [1500 X 2400] | -----
[5 empty] | 0 |  | 0 |  | 0 | [10 empty] | 0 |  |  |  |  | 0 |  |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [10 empty] | 0 |  |  |  |  | 0 |  |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [10 empty] | 0 |  |  |  |  | 0 |  |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [10 empty] | 0 |  |  |  |  | 0 |  |  |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 26 IN. WIDE

## SS237300-04
AIR WASHER SCHEDULE | [28 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | TYPE | AIR FLOW |  | MAX FACE VELOCITY |  | APD |  | TEMPERATURES | [7 empty] | % EFF | SPRAY PUMP |  |  |  | MIN BLEEDOFF |  | OVERALL DIMENSIONS (HEIGHT BY WIDTH) |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[11 empty] | EAT Db |  | EAT Wb |  | LAT Db |  | LAT Wb |  |  | NOMINAL POWER |  | PHASE | VOLT
[5 empty] | CFM | [L/s] | FPM | [M/s] | FT | [kPa] | °F | [°C] | °F | [°C] | °F | [°C] | °F | [°C] |  | HP | [W] |  |  | GPH | [L/h] | IN | [mm]
30-AW2 | ROOF | CENTRAL PLANT | 30-AHU1 | AIR WASHER | 12000 | 5700 | 400 | 2 | 0.5 | 130 | 105 | 40.6 | 70 | 21.1 | 74 | 23.3 | 70 | 21.1 | 90% | 1 | 750 | 1 | 115 | 25 | 95 | 60 X 72 | [1500 X 2400] | -----
[6 empty] | 0 |  | 0 |  | 0 | [10 empty] | 0 |  |  |  | 0
[6 empty] | 0 |  | 0 |  | 0 | [10 empty] | 0 |  |  |  | 0
[6 empty] | 0 |  | 0 |  | 0 | [10 empty] | 0 |  |  |  | 0
[6 empty] | 0 |  | 0 |  | 0 | [10 empty] | 0 |  |  |  | 0
[6 empty] | 0 |  | 0 |  | 0 | [10 empty] | 0 |  |  |  | 0
[6 empty] | 0 |  | 0 |  | 0 | [10 empty] | 0 |  |  |  | 0
[6 empty] | 0 |  | 0 |  | 0 | [10 empty] | 0 |  |  |  | 0
[6 empty] | 0 |  | 0 |  | 0 | [10 empty] | 0 |  |  |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 23 IN. WIDE

## SS238100-01
ROOM HEATING AND COOLING UNIT SCHEDULE (THRU-WALL ELECTRIC HEATING COIL, SELF-CONTAINED REFRIGERATION) | [17 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | NOMINAL HIGH SPEED AIR FLOW |  | COOLING CAPACITY | [7 empty] | COOLING ELECTRICAL POWER |  |  | MIN HEATING CAPACITY |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  |  | MIN TOTAL CAPACITY |  | MIN SENS CAPACITY |  | EAT |  |  |  | AMPS | PHASE | VOLT
[8 empty] | Db |  | Wb
|  | CFM | [L/s] | BTUH | [W] | BTUH | [W] | °F | [°C] | °F | [°C] |  |  |  | BTUH | [W]
7-PTAC3 | GROUND KEEPING SHED | 400 | 190 | 15000 | 4400 | 10600 | 3100 | 80 | 26.7 | 67 | 19.4 | 14.1 | 3 | 208 | 10350 | 3000 | -----
|  |  | 0 |  | 0 |  | 0 | [8 empty] | 0
|  |  | 0 |  | 0 |  | 0 | [8 empty] | 0
|  |  | 0 |  | 0 |  | 0 | [8 empty] | 0
|  |  | 0 |  | 0 |  | 0 | [8 empty] | 0
|  |  | 0 |  | 0 |  | 0 | [8 empty] | 0
|  |  | 0 |  | 0 |  | 0 | [8 empty] | 0
|  |  | 0 |  | 0 |  | 0 | [8 empty] | 0
|  |  | 0 |  | 0 |  | 0 | [8 empty] | 0
|  |  | 0 |  | 0 |  | 0 | [8 empty] | 0
NOTE
MINIMUM SENSIBLE CAPACITY BASED ON 100 ˚F [38 ˚C] OA.
DESIGNER NOTE
FINAL DRAWING SIZE = 14 IN.

## SS238100-02
WATER COOLED PACKAGED AIR CONDITIONER SCHEDULE | [30 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | TYPE | SUPPLY AIR FLOW |  | OUTSIDE AIR FLOW |  | EXT STATIC PRESSURE |  | COOLING CAPACITY | [8 empty] | CONDENSER WATER | [5 empty] | AIR FILTER MARK NO | ELECTRICAL POWER |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[10 empty] | MIN TOTAL CAPACITY |  | MIN SENS CAPACITY |  | EAT |  |  |  | MIN EER | EWT |  | FLOW |  | WPD |  |  | RLA |  | PHASE | VOLT
[14 empty] | Db |  | Wb
|  |  |  | CFM | [L/s] | CFM | [L/s] | IN | [Pa] | MBH | [kW] | MBH | [kW] | °F | [°C] | °F | [°C] |  | °F | [°C] | GPM | [L/s] | FT | [Pa] |  | Comp 1 | Comp 2
20-WCPU1 | ROOF | OFFICE ANNEX | PACKAGED ROOFTOP | 12000 | 5700 | 1800 | 850 | 1.5 | 380 | 360 | 1200 | 306 | 90 | 80 | 26.7 | 67 | 19.4 | 14.5 | 85 | 29.4 | 90 | 5.7 | 9 | 34 | 20-PF-1 | 36 | 54 | 3 | 208 | -----
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [8 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [8 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [8 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [8 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [8 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [8 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [8 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [8 empty] | 0 |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 20 IN. WIDE

## SS238100-03
SINGLE PACKAGED AIR CONDITIONER GAS/ELECTRIC SCHEDULE (ROOFTOP) | [37 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | TYPE | TOTAL SUPPLY AIR FLOW |  | MIN. OUTSIDE AIR FLOW |  | EXT STATIC PRESSURE |  | COOLING CAPACITY | [13 empty] | HEATING CAPACITY | [5 empty] | AIR FILTER MARK NO | ELECTRICAL DATA | [5 empty] | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[10 empty] | MIN TOTAL CAPACITY |  | MIN SENS CAPACITY |  | MIN SEER | EAT |  |  |  | OSA DESIGN TEMP |  | COMP Kw | GAS MIN. INPUT |  | MIN. NET OUTPUT |  | EAT Db |  | LAT Db |  |  | INDOOR FAN |  |  | UNIT POWER CONNECTION
[15 empty] | Db |  | Wb
|  |  |  | CFM | [L/s] | CFM | [L/s] | IN | [Pa] | MBH | [kW] | MBH | [kW] |  | °F | [°C] | °F | [°C] | °F | [°C] |  | MBH | [kW] | MBH | [kW] | °F | [°C] | °F | [°C] |  | HP | [W] | CONTROL | MCA | PHASE | VOLT
20-WCPU1 | ROOF | OFFICE ANNEX | PACKAGED ROOFTOP | 12000 | 5700 | 1800 | 850 | 1.5 | 380 | 360 | 1200 | 306 | 90 | 14.5 | 80 | 26.7 | 67 | 19.4 | 105 | 40.6 |  | 90 | 26 | 90 | 26 | 80 | 26.7 | 80 | 26.7 | 20-PF-1 | 36 | 27000 |  | 36 |  |  | -----
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [6 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [6 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [6 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [6 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [6 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [6 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [6 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [6 empty] | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 26 IN. WIDE

## SS238100-04
SINGLE PACKAGED AIR CONDITIONER HEAT PUMP SCHEDULE (ROOFTOP) | [43 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | TYPE | TOTAL SUPPLY AIR FLOW |  | MIN. OUTSIDE AIR FLOW |  | EXT STATIC PRESSURE |  | COOLING CAPACITY | [11 empty] | HEATING CAPACITY | [7 empty] | AIR FILTER MARK NO | ELECTRICAL DATA | [8 empty] | SUPPLEMENTAL HEAT |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[10 empty] | MIN TOTAL CAPACITY |  | MIN SENS CAPACITY |  | MIN SEER | EAT |  |  |  | OSA DESIGN TEMP |  | COMP Kw | MIN. HEAT CAPACITY |  | EAT DB |  | LAT Db |  | OSA DESIGN TEMP |  |  | INDOOR FAN |  |  | UNIT POWER CONNECTION |  |  | MCA | PHASE | VOLT
[15 empty] | Db |  | Wb
|  |  |  | CFM | [L/s] | CFM | [L/s] | IN | [Pa] | MBH | [kW] | MBH | [kW] |  | °F | [°C] | °F | [°C] | °F | [°C] |  | MBH | KW | °F | [°C] | °F | [°C] | °F | [°C] |  | HP | [W] | CONTROL | MCA | PHASE | VOLT |  |  |  | Kw | PHASE | VOLT
20-WCPU1 | ROOF | OFFICE ANNEX | PACKAGED ROOFTOP | 12000 | 5700 | 1800 | 850 | 1.5 | 380 | 360 | 1200 | 306 | 90 | 14.5 | 80 | 26.7 | 67 | 19.4 |  |  |  |  | 0 | 80 | 26.7 | 80 | 26.7 |  |  | 20-PF-1 | 36 | 27000 |  | 36 |  |  |  | 1 | 208/230 |  |  |  | -----
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 | [8 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 | [8 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 | [8 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 | [8 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 | [8 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 | [8 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 | [8 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 | [8 empty] | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 30 IN. WIDE

## SS238100-05
SPLIT SYSTEM AIR CONDITIONER GAS/ELECTRIC SCHEDULE | [37 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | TYPE | TOTAL SUPPLY AIR FLOW |  | MIN. OUTSIDE AIR FLOW |  | EXT STATIC PRESSURE |  | COOLING CAPACITY | [13 empty] | HEATING CAPACITY | [5 empty] | AIR FILTER MARK NO | ELECTRICAL DATA | [5 empty] | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[10 empty] | MIN TOTAL CAPACITY |  | MIN SENS CAPACITY |  | MIN SEER | EAT |  |  |  | OSA DESIGN TEMP |  | COMP Kw | GAS MIN. INPUT |  | MIN. NET OUTPUT |  | EAT Db |  | LAT Db |  |  | INDOOR FAN |  |  | OUTDOOR UNIT FAN
[15 empty] | Db |  | Wb
|  |  |  | CFM | [L/s] | CFM | [L/s] | IN | [Pa] | MBH | [kW] | MBH | [kW] |  | °F | [°C] | °F | [°C] | °F | [°C] |  | MBH | [kW] | MBH | [kW] | °F | [°C] | °F | [°C] |  | HP | [W] | CONTROL | MCA | [W] | CONTROL
20-WCPU1 | ROOF | OFFICE ANNEX | PACKAGED ROOFTOP | 12000 | 5700 | 1800 | 850 | 1.5 | 380 | 360 | 1200 | 306 | 90 | 14.5 | 80 | 26.7 | 67 | 19.4 |  |  |  | 90 | 26 | 90 | 26 | 80 | 26.7 | 80 | 26.7 | 20-PF-1 | 36 | 27000 |  | 36 | 27000 |  | -----
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [6 empty] | 0 |  |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 26 IN. WIDE

## SS238100-06
SPLIT SYSTEM AIR CONDITIONER HEAT PUMP SCHEDULE | [43 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | TYPE | TOTAL SUPPLY AIR FLOW |  | MIN. OUTSIDE AIR FLOW |  | EXT STATIC PRESSURE |  | COOLING CAPACITY | [11 empty] | HEATING CAPACITY | [7 empty] | AIR FILTER MARK NO | ELECTRICAL DATA | [8 empty] | SUPPLEMENTAL HEAT |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[10 empty] | MIN TOTAL CAPACITY |  | MIN SENS CAPACITY |  | MIN SEER | EAT |  |  |  | OSA DESIGN TEMP |  | COMP Kw | MIN. HEAT CAPACITY |  | EAT DB |  | LAT Db |  | OSA DESIGN TEMP |  |  | INDOOR FAN |  |  | OUTDOOR UNIT FAN |  |  | MCA | PHASE | VOLT
[15 empty] | Db |  | Wb
|  |  |  | CFM | [L/s] | CFM | [L/s] | IN | [Pa] | MBH | [kW] | MBH | [kW] |  | °F | [°C] | °F | [°C] | °F | [°C] |  | MBH | KW | °F | [°C] | °F | [°C] | °F | [°C] |  | HP | [W] | CONTROL | HP | [w] | CONTROL |  |  |  | Kw | PHASE | VOLT
20-WCPU1 | ROOF | OFFICE ANNEX | PACKAGED ROOFTOP | 12000 | 5700 | 1800 | 850 | 1.5 | 380 | 360 | 1200 | 306 | 90 | 14.5 | 80 | 26.7 | 67 | 19.4 |  |  |  |  | 0 | 80 | 26.7 | 80 | 26.7 |  |  | 20-PF-1 | 36 | 27000 |  | 36 | 27000 |  |  | 1 | 208/230 |  |  |  | -----
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 | [8 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 | [8 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 | [8 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 | [8 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 | [8 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 | [8 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 | [8 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  | 0 |  | 0 | [9 empty] | 0 | [8 empty] | 0 |  |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 30 IN. WIDE

## SS238146-01
WATER SOURCE HEAT PUMP SCHEDULE | [41 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | TYPE | AIR FLOW |  | OUTSIDE AIR FLOW |  | EXT STATIC PRESSURE |  | COOLING CAPACITY | [10 empty] | CIRCULATING WATER | [5 empty] | HEATING CAPACITY | [5 empty] | AIR FILTER MARK NO | ELECTRICAL | [7 empty] | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[10 empty] | EER | MIN TOTAL CAPACITY |  | MIN SENS CAPACITY |  | EAT |  |  |  | EWT |  | FLOW |  | WPD |  | RUNOUT SIZE |  | CAPACITY |  | EAT |  | EWT |  |  | FAN POWER |  | COMPRESSOR |  |  | PHASE | VOLT | REMARKS
[15 empty] | Db |  | Wb | [18 empty] | # COMP | NOMINAL POWER
|  |  |  | CFM | [L/s] | CFM | [L/s] | IN | [Pa] |  | BTUH | [W] | BTUH | [W] | °F | [°C] | °F | [°C] | °F | [°C] | GPM | [L/s] | FT | [Pa] | IN | [mm] | BTUH | [W] | °F | [°C] | °F | [°C] |  | HP | [W] |  | HP | [KW]
25-WCHP1 | ABOVE ROOM 11076 | ROOM 11076 | HORIZONTAL | 1100 | 520 | 120 | 57 | 0.8 | 200 | 14 | 36000 | 11000 | 29000 | 8500 | 80 | 26.7 | 66 | 18.9 | 86 | 30 | 8 | 0.5 | 6 | 150 | 1.5 | 38 | 40000 | 12000 | 68 | 20 | 68 | 20 | 25-PF-1 | 0.75 | 560 | 1 | 3 | 2.2 | 1 | 277
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
[5 empty] | 0 |  | 0 |  | 0 |  |  | 0 |  | 0 | [7 empty] | 0 |  | 0 |  | 0 |  | 0 | [6 empty] | 0 |  |  | 0
NOTE
COOLING CAPACITY BASED ON 85 ⁰F [29 ⁰ C] EWT.
DESIGNER NOTE
FINAL DRAWING SIZE = 30 IN. WIDE

## SS238200-01
HOT WATER UNIT HEATER SCHEDULE | [22 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | TYPE UNIT | AIR FLOW |  | MIN CAPACITY |  | TEMPERATURES |  |  |  | FLOW |  | WPD |  | CONTROL SEQUENCE | MOTOR |  |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[8 empty] | EAT |  | EWT | [6 empty] | POWER |  | PHASE | VOLT | RPM
|  |  |  | CFM | [L/s] | BTUH | [W] | °F | [°C] | °F | [°C] | GPM | [L/s] | FT | [Pa] |  | HP | [W]
7-HWUH1 | C105 | LOADING DOCK | HORIZONTAL | 1500 | 710 | 56000 | 16000 | 60 | 15.6 | 140 | 60 | 6 | 0.37854 | 6.5 | 160 | C-1 | 0.5 | 370 | 1 | 120 | 1750 | -----
[5 empty] | 0 |  | 0 | [5 empty] | 0 |  | 0 |  |  | 0
[5 empty] | 0 |  | 0 | [5 empty] | 0 |  | 0 |  |  | 0
[5 empty] | 0 |  | 0 | [5 empty] | 0 |  | 0 |  |  | 0
[5 empty] | 0 |  | 0 | [5 empty] | 0 |  | 0 |  |  | 0
[5 empty] | 0 |  | 0 | [5 empty] | 0 |  | 0 |  |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 16 IN. WIDE

## SS238200-02
HOT WATER FINNED TUBE RADIATION SCHEDULE | [18 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA SERVED | TYPE | ENCLOSURE TYPE | MOUNTING | ENCLOSURE LENGTH |  | CAPACITY |  | TEMPERATURES |  |  |  | FLOW |  | MAX WPD |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[10 empty] | EWT |  | LWT
[6 empty] | FT | [M] | BTUH | [W] | °F | [°C] | °F | [°C] | GPM | [L/s] | FT | [Pa]
1-FTR5 | B1100 | LOBBY | SINGLE ROW | SLOPED TOP | WALL | 8 | 2.4 | 9000 | 2600 | 180 | 82.2 | 140 | 60 | 0.5 | 0.031545 | 3 | 9 | -----
[7 empty] | 0 |  | 0 | [5 empty] | 0 |  | 0
[7 empty] | 0 |  | 0 | [5 empty] | 0 |  | 0
[7 empty] | 0 |  | 0 | [5 empty] | 0 |  | 0
[7 empty] | 0 |  | 0 | [5 empty] | 0 |  | 0
[7 empty] | 0 |  | 0 | [5 empty] | 0 |  | 0
[7 empty] | 0 |  | 0 | [5 empty] | 0 |  | 0
[7 empty] | 0 |  | 0 | [5 empty] | 0 |  | 0
[7 empty] | 0 |  | 0 | [5 empty] | 0 |  | 0
[7 empty] | 0 |  | 0 | [5 empty] | 0 |  | 0
NOTE
FIELD-VERIFY ENCLOSURE LENGTHS.
DESIGNER NOTE
1. FIN TUBE IS SIZED AT 1000 TO 1500 BTUH/LF.
2. FINAL DRAWING SIZE = 16 IN. WIDE

## SS238200-03
RADIANT CEILING PANEL SCHEDULE (ELECTRIC ) | [10 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | ROOM LOCATION | AREA SERVED | PANEL SIZE |  | CAPACITY |  | POWER SUPPLY |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
|  |  | IN | [mm] | BTUH | [W] | AMPS | PHASE | VOLT
2-ERP-1 | B1106 | OFFICE | 24 x 24 | [ 610 x 610 ] | 850 | 250 | 2.1 | 1 | 120 | ---
2-ERP-2 | B1108 | OFFICE | 24 x 24 | [ 610 x 610 ] | 1280 | 380 | 3.2 | 1 | 120 | ---
2-ERP-3 | B1109 | PT ROOM | 24 x 36 | [ 610 x 915 ] | 1280 | 380 | 3.2 | 1 | 120 | ---
2-ERP-4 | B1110 | CLINCAL EXAM | 24 x 36 | [ 610 x 915 ] | 1920 | 560 | 4.7 | 1 | 120 | ---
2-ERP-5 | B1111 | CLINICAL EXAM | 24 x 48 | [ 610 x 1219 ] | 1700 | 500 | 4.2 | 1 | 120 | ---
2-ERP-6 | B1112 | CLINICAL EXAM | 24 x 48 | [ 610 x 1219 ] | 2500 | 730 | 6.1 | 1 | 120 | ---
0
0
0
0
0
0
0
0
DESIGNER NOTE
FINAL DRAWING SIZE = 10 IN. WIDE

## SS238200-04
RADIANT CEILING PANEL SCHEDULE (HYDRONIC ) | [15 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | ROOM LOCATION | AREA SERVED | PANEL SIZE |  | HEATING | [9 empty] | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[5 empty] | HEATING CAPACITY |  | EWT |  | LWT |  | HOT WATER FLOWRATE |  | WPD
|  |  | IN | [mm] | BTUH | [W] | °F | [°C] | °F | [°C] | GPM | [L/m] | FT | [kPa]
7-HRP2 | B1101 | CLINICAL EXAM | 48 X 24 | [ 1200 X 600 ] | 12000 | 3500 | 180 | 82.2 | 155 | 68.3 | 1 | 3.8 | 8 | 24 | ----
[6 empty] | 0 | [5 empty] | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0
[6 empty] | 0 | [5 empty] | 0 |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 12 IN. WIDE

## SS238200-05
STEAM UNIT HEATER SCHEDULE | [24 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA SERVED | TYPE UNIT | AIR FLOW |  | EAT |  | MIN CAPACITY |  | STEAM | [5 empty] | TRAP |  | CONTROL SEQUENCE | MOTOR |  |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[10 empty] | PRESS ENT VALVE |  | PRESS ENT HEATER |  | FLOW |  |  |  |  | NOMINAL POWER |  | PHASE | VOLT | RPM
|  |  |  | CFM | [L/s] | °F | [°C] | BTUH | [W] | PSIG | [kPa] | PSIG | [kPa] | LBS/HR | [kg/HR] | LBS/HR | [kg/HR] |  | HP | [W]
1-SUH7 | G1100 | STORAGE | HORIZONTAL | 600 | 280 | 40 | 4.4 | 32000 | 9400 | 15 | 100 | 9 | 62 | 34 | 15 | 68 | 31 | C-1 | 0.5 | 370 | 1 | 120 | 1750 | ---
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 20 IN. WIDE
UPDATED: 12/1/2017

## SS238200-06
COOLING ONLY TWO PIPE FAN COIL UNIT SCHEDULE | [30 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | TYPE | FAN AIR FLOW |  | EXTERNAL APD |  | COOLING REQUIREMENTS | [7 empty] | CIRCULATING WATER | [7 empty] | FILTER | FAN MOTOR | [5 empty] | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[7 empty] | MIN SENS CAPACITY |  | MIN TOTAL CAPACITY |  | EAT |  |  |  | FLOW |  | EWT |  | WPD |  | RUNOUT SIZE |  |  | POWER |  | PHASE | VOLT | RPM | SPEED CONTROL
[11 empty] | Db |  | Wb
|  |  | CFM | [L/s] | IN WG | [Pa] | BTUH | [W] | BTUH | [W] | °F | [°C] | °F | [°C] | GPM | [L/s] | °F | [°C] | FT | [kPa] | IN | [mm] | MERV RATING | HP | [W]
1-FCUC1 | B1100 | HORIZONTAL | 1800 | 850 | 0.8 | 200 | 54000 | 16000 | 62000 | 18000 | 85 | 29.4 | 69 | 20.6 | 8 | 0.5 | 42 | 5.6 | 10 | 30 | 1.5 | 38 | 8 | 2 | 1500 | 3 | 460 | 1750 | SEE NOTE | -----
1-FCUC3 | B1105 | FLOOR MOUNT | 320 | 150 | 0.06 | 15 | 7800 | 2300 | 9600 | 2800 | 85 | 29.4 | 69 | 20.6 | 1.5 | 0.1 | 42 | 5.6 | 10 | 30 | 0.75 | 19 | 8 | 0.25 | 190 | 1 | 120 | 1750 | SEE NOTE | -----
1-FCUC6 | B1108 | VERTICAL | 600 | 280 | 0.06 | 15 | 15000 | 4400 | 18000 | 5300 | 85 | 29.4 | 69 | 20.6 | 2.4 | 0.2 | 42 | 5.6 | 10 | 30 | 1 | 25 | 8 | 0.75 | 560 | 1 | 208 | 1750 | SEE NOTE | -----
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  |  | 0
NOTE
MANUAL SPEED CONTROL WITH A SELECTOR SWITCH. | [30 empty] | #REF!
DESIGNER NOTE
1. COIL SHALL BE SELECTED AT 14⁰F [-10 ⁰C] WATER TEMPERATURE RISE.
2. FINAL DRAWING = 23 IN. WIDE

## SS238200-07
HEATING ONLY TWO PIPE FAN COIL UNIT SCHEDULE | [26 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | TYPE | FAN AIR FLOW |  | EXTERNAL APD |  | HEATING REQUIREMENTS |  |  |  | CIRCULATING WATER | [7 empty] | FILTER | FAN MOTOR | [5 empty] | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[7 empty] | MIN CAPACITY |  | EAT, Db |  | FLOW |  | EWT |  | WPD |  | RUNOUT SIZE |  |  | POWER |  | PHASE | VOLT | RPM | SPEED CONTROL
|  |  | CFM | [L/s] | IN WG | [Pa] | BTUH | [W] | °F | [°C] | GPM | [L/s] | °F | [°C] | FT | [kPa] | IN | [mm] | MERV RATING | HP | [W]
1-FCUH14 | A1100 | VERTICAL | 400 | 190 | 0.06 | 15 | 21000 | 6200 | 45 | 7.2 | 2 | 26 | 180 | 82.2 | 10 | 30 | 0.75 | 19 | 8 | 0.25 | 190 | 1 | 208 | 1750 | SEE NOTE | ----
1-FCUH15 | A1101 | HORIZONTAL | 800 | 380 | 0.06 | 15 | 41000 | 12000 | 45 | 7.2 | 4 | 53 | 180 | 82.2 | 10 | 30 | 1 | 25 | 8 | 0.33 | 250 | 1 | 208 | 1750 | SEE NOTE | ----
1-FCUH16 | A1102 | FLOOR MOUNT | 1100 | 520 | 0.06 | 15 | 58000 | 17000 | 45 | 7.2 | 6 | 79 | 180 | 82.2 | 10 | 30 | 1.25 | 31 | 8 | 0.75 | 560 | 1 | 208 | 1750 | SEE NOTE | ----
|  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
NOTE
MANUAL SPEED CONTROL WITH A SELECTOR SWITCH.
DESIGNER NOTE
1. COIL SHALL BE SELECTED AT 20 ⁰F [-7 ⁰C] WATER TEMPERATURE DROP.
2. FINAL DRAWING = 20 IN. WIDE

## SS238200-08
FOUR PIPE FAN COIL UNIT SCHEDULE | [42 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | TYPE | FAN AIR FLOW |  | EXTERNAL APD |  | COOLING REQUIREMENTS | [15 empty] | HEATING REQUIREMENTS | [11 empty] | FILTER | FAN MOTOR | [6 empty] | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[7 empty] | MIN SENS CAPACITY |  | MIN TOTAL CAPACITY |  | EAT |  |  |  | FLOW |  | EWT |  | WPD |  | RUNOUT SIZE |  | MIN CAPACITY |  | EAT Db |  | FLOW |  | EWT |  | WPD |  | RUNOUT SIZE |  |  | POWER |  | PHASE | VOLT | RPM | SPEED CONTROL | REMARKS
[11 empty] | Db |  | Wb
|  |  | CFM | [L/s] | IN WG | [Pa] | BTUH | [W] | BTUH | [W] | °F | [°C] | °F | [°C] | GPM | [L/s] | °F | [°C] | FT | [kPa] | IN | [mm] | BTUH | W | °F | [°C] | GPM | [L/m] | °F | [°C] | FT | [kPa] | IN | [mm] | MERV RATING | HP | [W]
7-FCU1 | D1107 | VERTICAL | 1800 | 850 | 0.8 | 200 | 54000 | 16000 | 62000 | 18000 | 85 | 29.4 | 69 | 20.6 | 12 | 160 | 42 | 5.6 | 10 | 30 | 1.5 | 38 | 80000 | 23000 | 45 | 7.2 | 8.5 | 32 | 180 | 82.2 | 10 | 30 | 1.25 | 31 | 8 | 1.5 | 1100 | 3 | 208 | 1750 | CONSTANT | ----
7-FCU2 | D1108 | HORIZONTAL | 1100 | 520 | 0.5 | 130 | 26000 | 7600 | 32000 | 9400 | 85 | 29.4 | 69 | 20.6 | 6 | 79 | 42 | 5.6 | 10 | 30 | 1.25 | 31 | 58000 | 17000 | 45 | 7.2 | 6 | 23 | 180 | 82.2 | 10 | 30 | 1.25 | 31 |  | 1 | 750 | 3 | 208 | 1750 | CONSTANT
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
|  |  |  | 0 |  | 0 |  | 0 |  | 0 | [5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0 |  | 0 |  |  | 0
NOTES
MANUAL SPEED CONTROL WITH A SELECTOR SWITCH.
DESIGNER NOTES
1. COOLING COILS SHALL BE SELECTED AT A MINIMUM OF 14 ⁰F [-10 ⁰C] WATER TEMPERATURE RISE.
2. HEATING COILS SHALL BE SELECTED AT A MINIMUM OF 20 ⁰F [-7 ⁰C] WATER TEMPERATURE DROP.
3. FINAL DRAWING SIZE = 30 IN. WIDE

## SS238200-09
ELECTRIC DUCT MOUNTED HEATER SCHEDULE | [19 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | SYSTEM AND/OR SERVICE | TYPE | AIR FLOW |  | EAT |  | APD |  | DUCT SIZE |  |  |  | CAPACITY |  | POWER |  | CONTROL TYPE | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[10 empty] | LENGTH |  | WIDTH
|  |  |  | CFM | [L/s] | °F | [°C] | IN WG | [Pa] | IN | [mm] | IN | [mm] | BTUH | [W] | PHASE | VOLT
1-EDH7 | B1100 | 1-AHU2 | OPEN COIL, HELICAL RESISTANCE ELEMENTS | 1000 | 470 | 60 | 15.6 | 0.15 | 38 | 12 | 300 | 12 | 300 | 32000 | 9400 | 1 | 277 | SCR | ----
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0
[5 empty] | 0 |  |  |  | 0 |  | 0 |  | 0 |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 16 IN. WIDE

## SS238200-10
ELECTRIC UNIT HEATER SCHEDULE | [17 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | TYPE | AIR FLOW |  | EAT |  | MIN CAPACITY |  | POWER |  |  | FAN MOTOR |  |  |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[13 empty] | FAN POWER |  | PHASE | VOLT
|  |  |  | CFM | L/S | °F | [°C] | BTUH | [W] | AMP | PHASE | VOLT | HP | [W]
1-EUH5 | G1101 | MAINTENANCE | HORIZONTAL COIL RESISTANCE | 1350 | 640 | 25 | -3.9 | 70000 | 21000 | 30 | 3 | 460 | 0.5 | 370 | 3 | 460 | ----
[5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0
[5 empty] | 0 |  |  |  | 0 |  |  |  |  | 0
DESIGNER NOTE
FINAL DRAWING SIZE = 14 IN. WIDE

## SS238216-01
CHILLED WATER COOLING COIL SCHEDULE | [30 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | AIR FLOW |  | MAX FACE VELOCITY |  | APD |  | EAT |  |  |  | LAT |  |  |  | TOTAL CAPACITY |  | SENSIBLE CAPACITY |  | CHILLED WATER | [7 empty] | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[10 empty] | Db |  | Wb |  | Db |  | Wb | [5 empty] | FLOW |  | EWT |  | LWT |  | WPD
|  |  |  | CFM | [L/s] | FPM | [M/s] | IN WG | [Pa] | °F | [°C] | °F | [°C] | °F | [°C] | °F | [°C] | MBH | [kW] | MBH | [kW] | GPM | [L/s] | °F | [°C] | °F | [°C] | FT | [M]
7-CWCC5 | B1100AA | OUTPATIENT ADDITION | 7-AHU5 | 10000 | 4700 | 450 | 2.3 | 0.65 | 160 | 80 | 26.7 | 67 | 19.4 | 55 | 12.8 | 54 | 12.2 | 380 | 110 | 270 | 79 | 47 | 3 | 42 | 5.6 | 58 | 14.4 | 6 | 1.8 | -----
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0
NOTE
THE COOLING COIL FIN SPACING SHALL NOT EXCEED 132 FINS PER FOOT [400 FINS PER METER].
DESIGNER NOTES
1. ALL CHILLED WATER COOLING COILS SHALL BE SELECTED AT A MINIMUM OF 16 ˚F [-9 ˚C] WATER TEMPERATURE RISE.
2. FINAL DRAWING SIZE = 23 IN. WIDE

## SS238216-02
HOT WATER HEATING COIL SCHEDULE | [26 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | APPLICATION | AIR FLOW |  | MAX FACE VELOCITY |  | APD |  | TEMPERATURES |  |  |  | TOTAL MIN CAPACITY |  | HOT WATER | [7 empty] | % GLYCOL | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[11 empty] | EAT |  | LAT |  |  |  | FLOW |  | EWT |  | LWT |  | WPD
[5 empty] | CFM | [L/s] | FPM | [M/s] | IN WG | [Pa] | °F | [°C] | °F | [°C] | MBH | [kW] | GPM | [L/s] | °F | [°C] | °F | [°C] | FT | [kPa]
1-HWHC7 | G1100 | CLINICAL ADDITION | 1-AHU7 | PREHEAT | 10000 | 4700 | 450 | 2.3 | 0.2 | 50 | 45 | 7.2 | 90 | 32.2 | 480 | 1600 | 49 | 3.1 | 160 | 71.1 | 140 | 60 | 8 | 24 | 0 | ---
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [5 empty] | 0 |  | 0 | [5 empty] | 0
DESIGNER NOTES
1. INDICATE WHETHER GLYCOL IS USED.
2. FINAL DRAWING SIZE = 20 IN. WIDE

## SS238216-03
STEAM HEATING COIL SCHEDULE | [26 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | APPLICATION | AIR FLOW |  | MAX FACE VELOCITY |  | APD |  | TEMPERATURES |  |  |  | TOTAL MIN CAPACITY |  | STEAM | [8 empty] | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[11 empty] | EAT |  | LAT |  |  |  | ENT CONT VALVE |  | ENT COIL |  | FLOW |  | STEAM TRAP
[5 empty] | CFM | [L/s] | FPM | [M/s] | IN WG | [Pa] | °F | [°C] | °F | [°C] | MBH | [kW] | PSIG | [kPa] | PSIG | [kPa] | LBS/HR | [kg/HR] | MARK | LBS/HR | [kg/HR]
1-SHC16 | G1100 | CLINICAL ADDITION | 1-AHU7 | PREHEAT | 10000 | 4700 | 500 | [2.54] | 0.2 | 50 | 45 | 7.2 | 90 | 32.2 | 480 | 1600 | 15 | 100 | 5 | 35 | 500 | 230 | 1-TP7 | 1200 | 540 | ----
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
[6 empty] | 0 |  |  |  | 0 | [5 empty] | 0 |  | 0 |  | 0 |  | 0 |  |  | 0
DESIGNER NOTES
1. FOR TYPE STEAM COIL, INDICATE SINGLE TUBE, STEAM DISTRIBUTION, OR INTEGRAL FACE AND BYPASS. MAXIMUM S. P. LOSS SHALL NOT EXCEED 0.25 IN [6 Pa]. FOR IFB COILS, THIS TRANSLATES TO A MAXIMUM FACE VELOCITY OF 500 FPM [2.5 M/s].
2. DRAWING SIZE = 20 IN. WIDE
UPDATED: 12/1/2017

## SS238216-04
DIRECT EXPANSION COOLING COIL SCHEDULE | [25 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG SERVED | SYSTEM AND/OR SERVICE | AIR FLOW |  | MAX FACE VELOCITY |  | APD |  | EAT |  |  |  | LAT |  |  |  | TOTAL CAPACITY |  | SENSIBLE CAPACITY |  | REFRIGERANT | SATURATED SUCTION TEMP |  | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[10 empty] | Db |  | Wb |  | Db |  | Wb
|  |  |  | CFM | [L/s] | FPM | [M/s] | IN WG | [Pa] | °F | [°C] | °F | [°C] | °F | [°C] | °F | [°C] | MBH | [kW] | MBH | [kW] |  | °F | [°C]
1-DXCC5 | G1100B | CLINICAL | 1-ACCU1 | 10000 | 4700 | 450 | 0.8 | 0.65 | 160 | 80 | 26.7 | 67 | 19.4 | 55 | 12.8 | 54 | 12.2 | 390 | 1300 | 370 | 1300 | 410A | 44 | 6.7 | ---
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
[5 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0
DESIGNER NOTES
1. MAX FIN SPACING SHALL BE 132 FINS PER FOOT [400 FINS PER METER].
2. FINAL DRAWING SIZE = 19 IN. WIDE

## SS238216-05
HEAT RECOVERY SYSTEM RUN AROUND WATER COIL SCHEDULE | [33 empty] | DATA TO BE FILLED OUT AT CLOSEOUT
MARK | LOCATION | AREA AND/OR BLDG | SYSTEM AND/OR SERVICE | APPLICATION | AIR FLOW |  | MAX FACE VELOCITY |  | APD |  | EAT |  |  |  | LAT |  |  |  | TOTAL MIN CAPACITY |  | GLYCOL | [7 empty] | PUMP NO | PUMP HP | PHASE | VOLT | REMARKS | MANUFACTURER | MODEL NO | SERIAL NO | SUBMITTAL 1 TRACKING NO | SUBMITTAL 2 TRACKING NO | COMMISSIONING REPORT NO | TEST AND BALANCE DATA | OPS AND MAINT MANUAL TAB NO | PM NO
[11 empty] | Db |  | Wb |  | Db |  | Wb |  |  |  | FLOW |  | EGT |  | LGT |  | WPD
[5 empty] | CFM | [L/s] | FPM | [M/s] | IN WG | [Pa] | °F | [°C] | °F | [°C] | °F | [°C] | °F | [°C] | MBH | [kW] | GPM | [L/s] | °F | [°C] | °F | [°C] | FT | [kPa]
1-ERC1 | B908 | 3 NORTH | 1-AHU5 | SUPPLY COIL | 12000 | 5700 | 400 | 2 | 0.3 | 75 | 30 | -1.1 | 20 | -6.7 | 50 | 10 | 33 | 0.6 | 259 | 880 | 26 | 1.6 | 62 | 16.7 | 42 | 5.6 | 12 | 36 | 1-P7 | 0.75 | 1 | 208 | WINTER CONDITION
1-ERC2 | B906 | 3 NORTH | 1-AHU5 | EXHAUST COIL | 10000 | 4700 | 400 | 2 | 0.3 | 75 | 75 | 23.9 | 50 | 10 | 55 | 12.8 | 55 | 12.8 | 216 | 740 | 26 | 1.6 | 42 | 5.6 | 62 | 16.7 | 12 | 36
[6 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [5 empty] | 0
[6 empty] | 0 |  | 0 |  | 0 | [9 empty] | 0 |  | 0 | [5 empty] | 0
NOTES
1. CIRCULATING FLUID SHALL BE PROPYLENE GLYCOL, 50% CONCENTRATION.
2. PROVIDE A VA GRADE A PREFILTER AT EXHAUST COIL INLET.
DESIGNER NOTE
FINAL DRAWING SIZE = 26 IN. WIDE