SECTION 10 44 13
FIRE EXTINGUISHER CABINETS

SPEC WRITER NOTE:

1. Delete between //‑‑‑‑// If not applicable to project. Also delete any other item or paragraph not applicable in the section and renumber the paragraphs.

2. Use fully recessed cabinets. Do not allow projection of doors and frames into corridor areas other than frame flange thickness.

3. Insure details show cabinet recessed in wall with no penetration of fire rating when applicable.

4. Insure detail shows elevation of cabinet with glazing.

PART 1 ‑ GENERAL

1.1 DESCRIPTION

 This section covers recessed fire extinguisher cabinets.

1.2 RELATED WORK

A. Acrylic glazing: Section 08 80 00, GLAZING.

B. Field Painting: Section 09 91 00, PAINTING.

1.3 SUBMITTALS

A. Submit in accordance with Section 01 33 23, SHOP DRAWINGS, PRODUCT DATA, AND SAMPLES.

B. Manufacturer's Literature and Data: Fire extinguisher cabinet including installation instruction and rough opening required.

1.4 APPLICATION PUBLICATIONS

A. The publications listed below form a part of this specification to the extent referenced. The publications are referenced in the text by the basic designation only.

B. American Society of Testing and Materials (ASTM):

D4802-15 Poly (Methyl Methacrylate) Acrylic Plastic Sheet

PART 2 ‑ PRODUCTS

2.1 FIRE EXTINGUISHER CABINET

 Recessed type with flat trim of size and design shown.

2.2 FABRICATION

A. Form body of cabinet from 0.9 mm (0.0359 inch) thick sheet steel.

B. Fabricate door and trim from 1.2 mm (0.0478 inch) thick sheet steel with all face joints fully welded and ground smooth.

1. Glaze doors with 6 mm (1/4 inch) thick ASTM D4802, clear acrylic sheet, Category B-1, Finish 1.

2. Design doors to open 180 degrees.

3. Provide continuous hinge, pull handle, and adjustable roller catch.

2.3 FINISH

A. Finish interior of cabinet body with baked-on semigloss white enamel.

B. Finish door, frame with manufacturer's standard baked-on prime coat suitable for field painting.

PART 3 - EXECUTION

A. Install fire extinguisher cabinets in prepared openings and secure in accordance with manufacturer's instructions.

B. Install cabinet so that the extinguisher height within meets the requirements of NFPA 10

- - - E N D - - -